## Sheet1
LOAD CONDITION |  | TEMP | ICE | WIND | OVERLOAD FACTORS
Description |  | °F | Radial (in) | Pressure (psf) | ANGLE | TRANSVERSE | VERTICAL | LONGITUINDAL
1 - NESC LIGHT (250B) |  | 30 | 0 | 9 | 1.65 | 2.5 | 1.5 | 1.65
2 - NESC EXTREME WIND (250C) |  | 60 | 0 | 28.22 | 1.1 | 1.1 | 1.1 | 1.2
3 - NESC COMBINED ICE & WIND (250D) |  | 15 | 0.5 | 2.3 | 1 | 1 | 1 | 1
4 - NORMAL EVERYDAY |  | 60 | 0 | 0 | 1 | 1 | 1 | 1
5 - 2% POLE DEFLECTION |  | 60 | 0 | 0 | 1 | 1 | 1 | 1
6 - BROKEN PHASE |  | 60 | 0 | 0 | 1.1 | 1.1 | 1.1 | 1.1
7 - FULL BREAK (NESC 250D |  | 15 | 0.5 | 2.3 | 1 | 1 | 1 | 1
LC 12 | [8 empty] | LC 6 |  |  |  |  | LC 18
LOAD CASE ID: |  | LC1, NESC LIGHT (250B) | [6 empty] | LOAD CASE ID: |  | LC2, NESC EXTREME WIND (250C) |  |  | LOAD CASE ID: |  | LC3, NESC COMBINED ICE AND WIND (250D)
WIND ON STRUCTURE: |  | 9 | [6 empty] | WIND ON STRUCTURE: |  | 28.22 |  |  | WIND ON STRUCTURE: |  | 2.3
ATTACHMENT | V | T | L | [5 empty] | ATTACHMENT | V | T | L |  | ATTACHMENT | V | T | L
S1 | 500 | -1700 | 0 | [5 empty] | S1 | 400 | -1500 | 0 |  | S1 | 500 | -100 | -100
P1,A | 1200 | -4800 | 100 |  |  |  |  | 4948.7372 | P1,A | 900 | -4300 | 100 | 4394.3145 | P1,A | 1300 | -2800 | 100 | 3088.689
P1,B | 1200 | -4800 | 100 |  |  |  |  | 4948.7372 | P1,B | 900 | -4300 | 100 | 4394.3145 | P1,B | 1300 | -2800 | 100 | 3088.689
P1,C | 1200 | -4800 | 100 |  |  |  |  | 4948.7372 | P1,C | 900 | -4300 | 100 | 4394.3145 | P1,C | 1300 | -2800 | 100 | 3088.689
F1 | 100 | -500 | 100 | [5 empty] | F1 | 100 | -600 | 100 |  | F1 | 300 | -300 | 0
D1,A & D2,A | 300 | -1700 | 100 |  |  |  |  | 1729.1616 | D1,A & D2,A | 200 | -1500 | 100 |  | D1,A & D2,A | 400 | -1000 | 0
D1,B & D2,B | 300 | -1700 | 100 |  |  |  |  | 1729.1616 | D1,B & D2,B | 200 | -1500 | 100 |  | D1,B & D2,B | 400 | -1000 | 0
D1,C & D2,C | 300 | -1700 | 100 |  |  |  |  | 1729.1616 | D1,C & D2,C | 200 | -1500 | 100 |  | D1,C & D2,C | 400 | -1000 | 0
N1 & N2 | 200 | -600 | 100 | [5 empty] | N1 & N2 | 100 | -700 | 100 |  | N1 & N2 | 300 | -400 | 0
C1 | 100 | -800 | 100 |  |  |  |  | 812.4038 | C1 | 100 | -1100 | 100 | 1109.0537 | C1 | 300 | -400 | 100 | 509.902
C2 | 100 | -800 | 100 |  |  |  |  | 812.4038 | C2 | 100 | -1100 | 100 | 1109.0537 | C2 | 300 | -400 | 100 | 509.902
C3 | 100 | -800 | 100 |  |  |  |  | 812.4038 | C3 | 100 | -1100 | 100 | 1109.0537 | C3 | 300 | -400 | 100 | 509.902
C4 | 100 | -800 | 100 |  |  |  |  | 812.4038 | C4 | 100 | -1100 | 100 | 1109.0537 | C4 | 300 | -400 | 100 | 509.902
ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S | [6 empty] | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S |  |  | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S
LC 126 | [8 empty] | LC 125 |  |  |  |  | LC 114
LOAD CASE ID: |  | LC4, NORMAL EVERYDAY | [6 empty] | LOAD CASE ID: |  | LC 5, 2% POLE DEFLECTION |  |  | LOAD CASE ID: |  | LC6, BROKEN PHASE
WIND ON STRUCTURE: |  | 0 | [6 empty] | WIND ON STRUCTURE: |  | 0 |  |  | WIND ON STRUCTURE: |  | 0
ATTACHMENT | V | T | L | [5 empty] | ATTACHMENT | V | T | L |  | ATTACHMENT | V | T | L
S1 | 300 | -700 | -100 | [5 empty] | S1 | 300 | -600 | -100 |  | S1 | 300 | -800 | -100
P1,A | 800 | -1800 | 0 |  |  |  |  | 1969.7716 | P1,A | 800 | -1800 | 0 | 1969.7716 | P1,A | 900 | -1900 | 0 | 2102.3796
P1,B | 800 | -1800 | 0 |  |  |  |  | 1969.7716 | P1,B | 800 | -1800 | 0 | 1969.7716 | P1,B | 900 | -1900 | 0 | 2102.3796
P1,C | 800 | -1800 | 0 |  |  |  |  | 1969.7716 | P1,C | 800 | -1800 | 0 | 1969.7716 | P1,C | 900 | -1900 | 0 | 2102.3796
F1 | 100 | -100 | 0 | [5 empty] | F1 | 100 | -100 | 0 |  | F1 | 100 | -100 | 0
D1,A & D2,A | 200 | -600 | 0 | [5 empty] | D1,A & D2,A | 200 | -400 | 0 |  | D1,A & D2,A | 200 | -600 | 0
D1,B & D2,B | 200 | -600 | 0 | [5 empty] | D1,B & D2,B | 200 | -400 | 0 |  | D1,B & D2,B | 200 | -600 | 0
D1,C & D2,C | 200 | -600 | 0 | [5 empty] | D1,C & D2,C | 200 | -400 | 0 |  | D1,C & D2,C | 200 | -600 | 0
N1 & N2 | 100 | -100 | 0 | [5 empty] | N1 & N2 | 100 | -100 | 0 |  | N1 & N2 | 100 | -100 | 0
C1 | 100 | -100 | 0 | [5 empty] | C1 | 100 | -100 | 0 |  | C1 | 100 | -100 | 0
C2 | 100 | -100 | 0 | [5 empty] | C2 | 100 | -100 | 0 |  | C2 | 100 | -100 | 0
C3 | 100 | -100 | 0 | [5 empty] | C3 | 100 | -100 | 0 |  | C3 | 100 | -100 | 0
C4 | 100 | -100 | 0 | [5 empty] | C4 | 100 | -100 | 0 |  | C4 | 100 | -100 | 0
ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S | [6 empty] | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S POLE TOP DEFLECTION LIMITED TO 2% OF POLE HEIGHT. |  |  | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S

## Sheet2
Row # | LC # | WC # | Load Case Description | Set No. | Phase No. | Attach. Joint Labels | Structure Loads Vert. (lbs) | Structure Loads Trans. (lbs) | Structure Loads Long. (lbs) | Loads from back span Vert. (lbs) | Loads from back span Trans. (lbs) | Loads from back span Long. (lbs) | Loads from ahead span Vert. (lbs) | Loads from ahead span Trans. (lbs) | Loads from ahead span Long. (lbs) | Warnings
| 1 | 12 | Hurricane NL+ | 1 | 1 | TL-S1 | 299 | -566 | -3 | 164 | -294 | 4476 | 135 | -271 | -4479 |  | 589.2886
| 1 | 12 | Hurricane NL+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 1 | 12 | Hurricane NL+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 1 | 12 | Hurricane NL+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 1 | 12 | Hurricane NL+ | 10 | 1 | ST1 | 802 | -1132 | -5 | 421 | -591 | 14333 | 381 | -541 | -14338 |  | 1207.7624
| 1 | 12 | Hurricane NL+ | 10 | 2 | ST2 | 802 | -1146 | -5 | 421 | -598 | 14332 | 381 | -549 | -14337 |  | 1220.8939
| 1 | 12 | Hurricane NL+ | 10 | 3 | ST3 | 802 | -1162 | -5 | 421 | -605 | 14331 | 381 | -557 | -14336 |  | 1235.9248
| 1 | 12 | Hurricane NL+ | 46 | 1 | F2 | 64 | 100 | -1 | 34 | 43 | 1241 | 30 | 57 | -1242 |  | 105.6267
| 1 | 12 | Hurricane NL+ | 49 | 1 | S1 | 165 | -405 | -2 | 90 | -213 | 4645 | 75 | -192 | -4647 |  | 414.8843
| 1 | 12 | Hurricane NL+ | 49 | 2 | S2 | 165 | -409 | -2 | 90 | -215 | 4645 | 75 | -194 | -4647 |  | 418.7899
| 1 | 12 | Hurricane NL+ | 49 | 3 | S3 | 165 | -414 | -2 | 90 | -217 | 4645 | 75 | -197 | -4647 |  | 423.6744
| 1 | 12 | Hurricane NL+ | 50 | 1 | S4 | 164 | -365 | -2 | 90 | -191 | 4646 | 75 | -173 | -4648 |  | 375.9375
| 1 | 12 | Hurricane NL+ | 50 | 2 | S5 | 164 | -368 | -2 | 90 | -193 | 4646 | 75 | -175 | -4648 |  | 378.8509
| 1 | 12 | Hurricane NL+ | 50 | 3 | S6 | 164 | -371 | -2 | 90 | -194 | 4646 | 75 | -176 | -4647 |  | 381.7656
| 1 | 12 | Hurricane NL+ | 53 | 1 | S7 | 79 | -33 | -1 | 42 | -23 | 1636 | 37 | -10 | -1637 |  | 53.4228
| 1 | 12 | Hurricane NL+ | 54 | 1 | S8 | 79 | -16 | -1 | 42 | -14 | 1636 | 37 | -3 | -1637 |  | 44.9555
| 1 | 12 | Hurricane NL+ | 57 | 1 | PT:P1 | 66 | 119 | -2 | 37 | 48 | 2284 | 29 | 71 | -2286 |  | 124.6355
| 1 | 12 | Hurricane NL+ | 58 | 1 | PT:P2 | 66 | 119 | -2 | 37 | 48 | 2281 | 29 | 71 | -2283 |  | 124.6355
| 1 | 12 | Hurricane NL+ | 59 | 1 | PT:P3 | 66 | 119 | -2 | 37 | 48 | 2278 | 29 | 71 | -2280 |  | 124.6355
| 1 | 12 | Hurricane NL+ | 60 | 1 | PT:P4 | 66 | 119 | -2 | 37 | 48 | 2276 | 29 | 71 | -2278 |  | 124.6355
| 2 | 12 | Hurricane NL- | 1 | 1 | TL-S1 | 299 | -1277 | -1 | 164 | -635 | 4441 | 135 | -641 | -4442 |  | 1287.4883
| 2 | 12 | Hurricane NL- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 2 | 12 | Hurricane NL- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 2 | 12 | Hurricane NL- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 2 | 12 | Hurricane NL- | 10 | 1 | ST1 | 802 | -3842 | 4 | 421 | -1893 | 14236 | 381 | -1948 | -14232 |  | 3864.9995
| 2 | 12 | Hurricane NL- | 10 | 2 | ST2 | 802 | -3817 | 4 | 421 | -1882 | 14237 | 381 | -1936 | -14233 |  | 3840.1492
| 2 | 12 | Hurricane NL- | 10 | 3 | ST3 | 802 | -3791 | 4 | 421 | -1869 | 14238 | 381 | -1923 | -14234 |  | 3814.307
| 2 | 12 | Hurricane NL- | 46 | 1 | F2 | 64 | -524 | 1 | 34 | -255 | 1215 | 30 | -270 | -1214 |  | 525.1028
| 2 | 12 | Hurricane NL- | 49 | 1 | S1 | 165 | -1275 | 2 | 90 | -628 | 4607 | 75 | -646 | -4606 |  | 1278.1741
| 2 | 12 | Hurricane NL- | 49 | 2 | S2 | 165 | -1271 | 2 | 90 | -627 | 4608 | 75 | -645 | -4606 |  | 1274.1841
| 2 | 12 | Hurricane NL- | 49 | 3 | S3 | 165 | -1268 | 2 | 90 | -625 | 4608 | 75 | -643 | -4606 |  | 1271.1916
| 2 | 12 | Hurricane NL- | 50 | 1 | S4 | 164 | -1232 | 2 | 90 | -605 | 4610 | 75 | -626 | -4609 |  | 1235.2846
| 2 | 12 | Hurricane NL- | 50 | 2 | S5 | 164 | -1228 | 2 | 90 | -603 | 4611 | 75 | -624 | -4609 |  | 1231.2953
| 2 | 12 | Hurricane NL- | 50 | 3 | S6 | 164 | -1223 | 2 | 90 | -601 | 4611 | 75 | -622 | -4609 |  | 1226.3087
| 2 | 12 | Hurricane NL- | 53 | 1 | S7 | 79 | -559 | 1 | 42 | -274 | 1613 | 37 | -285 | -1612 |  | 560.5765
| 2 | 12 | Hurricane NL- | 54 | 1 | S8 | 79 | -542 | 1 | 42 | -265 | 1615 | 37 | -277 | -1614 |  | 543.6258
| 2 | 12 | Hurricane NL- | 57 | 1 | PT:P1 | 66 | -920 | 2 | 37 | -448 | 2240 | 29 | -472 | -2238 |  | 920.7459
| 2 | 12 | Hurricane NL- | 58 | 1 | PT:P2 | 66 | -919 | 2 | 37 | -448 | 2237 | 29 | -471 | -2235 |  | 919.7467
| 2 | 12 | Hurricane NL- | 59 | 1 | PT:P3 | 66 | -918 | 2 | 37 | -447 | 2235 | 29 | -470 | -2232 |  | 918.7475
| 2 | 12 | Hurricane NL- | 60 | 1 | PT:P4 | 66 | -917 | 2 | 37 | -447 | 2232 | 29 | -470 | -2230 |  | 917.7483
| 3 | 12 | Hurricane NR+ | 1 | 1 | TL-S1 | 299 | -565 | -4 | 164 | -300 | 4475 | 135 | -265 | -4479 |  | 588.3341
| 3 | 12 | Hurricane NR+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 3 | 12 | Hurricane NR+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 3 | 12 | Hurricane NR+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 3 | 12 | Hurricane NR+ | 10 | 1 | ST1 | 802 | -1130 | -8 | 421 | -608 | 14331 | 381 | -522 | -14339 |  | 1205.9042
| 3 | 12 | Hurricane NR+ | 10 | 2 | ST2 | 802 | -1144 | -8 | 421 | -614 | 14331 | 381 | -530 | -14339 |  | 1219.0328
| 3 | 12 | Hurricane NR+ | 10 | 3 | ST3 | 802 | -1160 | -8 | 421 | -621 | 14330 | 381 | -539 | -14338 |  | 1234.0604
| 3 | 12 | Hurricane NR+ | 46 | 1 | F2 | 64 | 101 | -2 | 34 | 39 | 1241 | 30 | 62 | -1243 |  | 106.588
| 3 | 12 | Hurricane NR+ | 49 | 1 | S1 | 165 | -405 | -3 | 90 | -220 | 4645 | 75 | -185 | -4648 |  | 414.8903
| 3 | 12 | Hurricane NR+ | 49 | 2 | S2 | 165 | -409 | -3 | 90 | -222 | 4644 | 75 | -187 | -4648 |  | 418.7959
| 3 | 12 | Hurricane NR+ | 49 | 3 | S3 | 165 | -413 | -3 | 90 | -224 | 4644 | 75 | -189 | -4647 |  | 422.7032
| 3 | 12 | Hurricane NR+ | 50 | 1 | S4 | 164 | -364 | -3 | 90 | -198 | 4646 | 75 | -166 | -4648 |  | 374.9733
| 3 | 12 | Hurricane NR+ | 50 | 2 | S5 | 164 | -367 | -3 | 90 | -199 | 4645 | 75 | -168 | -4648 |  | 377.8862
| 3 | 12 | Hurricane NR+ | 50 | 3 | S6 | 164 | -370 | -3 | 90 | -200 | 4645 | 75 | -170 | -4648 |  | 380.8005
| 3 | 12 | Hurricane NR+ | 53 | 1 | S7 | 79 | -32 | -2 | 42 | -27 | 1635 | 37 | -6 | -1637 |  | 52.8394
| 3 | 12 | Hurricane NR+ | 54 | 1 | S8 | 79 | -16 | -2 | 42 | -18 | 1636 | 37 | 2 | -1638 |  | 44.9889
| 3 | 12 | Hurricane NR+ | 57 | 1 | PT:P1 | 66 | 120 | -4 | 37 | 40 | 2283 | 29 | 80 | -2287 |  | 125.6384
| 3 | 12 | Hurricane NR+ | 58 | 1 | PT:P2 | 66 | 120 | -4 | 37 | 40 | 2280 | 29 | 80 | -2284 |  | 125.6384
| 3 | 12 | Hurricane NR+ | 59 | 1 | PT:P3 | 66 | 120 | -4 | 37 | 40 | 2278 | 29 | 80 | -2281 |  | 125.6384
| 3 | 12 | Hurricane NR+ | 60 | 1 | PT:P4 | 66 | 120 | -4 | 37 | 40 | 2275 | 29 | 80 | -2279 |  | 125.6384
| 4 | 12 | Hurricane NR- | 1 | 1 | TL-S1 | 299 | -1277 | 1 | 164 | -629 | 4442 | 135 | -648 | -4441 |  | 1287.4883
| 4 | 12 | Hurricane NR- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 4 | 12 | Hurricane NR- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 4 | 12 | Hurricane NR- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 4 | 12 | Hurricane NR- | 10 | 1 | ST1 | 802 | -3844 | 8 | 421 | -1876 | 14238 | 381 | -1967 | -14230 |  | 3866.9938
| 4 | 12 | Hurricane NR- | 10 | 2 | ST2 | 802 | -3820 | 7 | 421 | -1865 | 14239 | 381 | -1955 | -14231 |  | 3843.1354
| 4 | 12 | Hurricane NR- | 10 | 3 | ST3 | 802 | -3794 | 7 | 421 | -1853 | 14240 | 381 | -1941 | -14233 |  | 3817.293
| 4 | 12 | Hurricane NR- | 46 | 1 | F2 | 64 | -525 | 2 | 34 | -250 | 1216 | 30 | -275 | -1214 |  | 526.1036
| 4 | 12 | Hurricane NR- | 49 | 1 | S1 | 165 | -1275 | 3 | 90 | -622 | 4608 | 75 | -654 | -4605 |  | 1278.176
| 4 | 12 | Hurricane NR- | 49 | 2 | S2 | 165 | -1272 | 3 | 90 | -620 | 4608 | 75 | -652 | -4605 |  | 1275.1835
| 4 | 12 | Hurricane NR- | 49 | 3 | S3 | 165 | -1269 | 3 | 90 | -619 | 4608 | 75 | -650 | -4606 |  | 1272.191
| 4 | 12 | Hurricane NR- | 50 | 1 | S4 | 164 | -1232 | 3 | 90 | -599 | 4611 | 75 | -633 | -4608 |  | 1235.2866
| 4 | 12 | Hurricane NR- | 50 | 2 | S5 | 164 | -1228 | 3 | 90 | -597 | 4611 | 75 | -631 | -4608 |  | 1231.2973
| 4 | 12 | Hurricane NR- | 50 | 3 | S6 | 164 | -1224 | 3 | 90 | -595 | 4611 | 75 | -629 | -4608 |  | 1227.308
| 4 | 12 | Hurricane NR- | 53 | 1 | S7 | 79 | -559 | 2 | 42 | -270 | 1613 | 37 | -290 | -1611 |  | 560.5792
| 4 | 12 | Hurricane NR- | 54 | 1 | S8 | 79 | -543 | 2 | 42 | -261 | 1615 | 37 | -282 | -1613 |  | 544.6256
| 4 | 12 | Hurricane NR- | 57 | 1 | PT:P1 | 66 | -921 | 3 | 37 | -441 | 2240 | 29 | -480 | -2237 |  | 921.7478
| 4 | 12 | Hurricane NR- | 58 | 1 | PT:P2 | 66 | -920 | 3 | 37 | -440 | 2238 | 29 | -480 | -2234 |  | 920.7486
| 4 | 12 | Hurricane NR- | 59 | 1 | PT:P3 | 66 | -919 | 3 | 37 | -439 | 2235 | 29 | -479 | -2232 |  | 919.7494
| 4 | 12 | Hurricane NR- | 60 | 1 | PT:P4 | 66 | -918 | 3 | 37 | -439 | 2233 | 29 | -479 | -2230 |  | 918.7502
| 5 | 12 | Hurricane BI+ | 1 | 1 | TL-S1 | 299 | -563 | -4 | 164 | -296 | 4475 | 135 | -266 | -4479 |  | 586.4137
| 5 | 12 | Hurricane BI+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 5 | 12 | Hurricane BI+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 5 | 12 | Hurricane BI+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 5 | 12 | Hurricane BI+ | 10 | 1 | ST1 | 802 | -1121 | -7 | 421 | -595 | 14332 | 381 | -526 | -14339 |  | 1197.4686
| 5 | 12 | Hurricane BI+ | 10 | 2 | ST2 | 802 | -1135 | -6 | 421 | -601 | 14332 | 381 | -534 | -14338 |  | 1210.5792
| 5 | 12 | Hurricane BI+ | 10 | 3 | ST3 | 802 | -1151 | -6 | 421 | -608 | 14331 | 381 | -543 | -14337 |  | 1225.5929
| 5 | 12 | Hurricane BI+ | 46 | 1 | F2 | 64 | 103 | -2 | 34 | 42 | 1241 | 30 | 61 | -1243 |  | 108.485
| 5 | 12 | Hurricane BI+ | 49 | 1 | S1 | 165 | -402 | -3 | 90 | -215 | 4645 | 75 | -187 | -4648 |  | 411.9624
| 5 | 12 | Hurricane BI+ | 49 | 2 | S2 | 165 | -406 | -3 | 90 | -217 | 4645 | 75 | -189 | -4647 |  | 415.8666
| 5 | 12 | Hurricane BI+ | 49 | 3 | S3 | 165 | -410 | -2 | 90 | -219 | 4645 | 75 | -191 | -4647 |  | 419.7666
| 5 | 12 | Hurricane BI+ | 50 | 1 | S4 | 164 | -361 | -2 | 90 | -193 | 4646 | 75 | -168 | -4648 |  | 372.0551
| 5 | 12 | Hurricane BI+ | 50 | 2 | S5 | 164 | -364 | -2 | 90 | -194 | 4646 | 75 | -169 | -4648 |  | 374.9667
| 5 | 12 | Hurricane BI+ | 50 | 3 | S6 | 164 | -367 | -2 | 90 | -196 | 4646 | 75 | -171 | -4648 |  | 377.8796
| 5 | 12 | Hurricane BI+ | 53 | 1 | S7 | 79 | -30 | -2 | 42 | -24 | 1636 | 37 | -7 | -1637 |  | 51.6527
| 5 | 12 | Hurricane BI+ | 54 | 1 | S8 | 79 | -14 | -1 | 42 | -15 | 1636 | 37 | 1 | -1638 |  | 44.2832
| 5 | 12 | Hurricane BI+ | 57 | 1 | PT:P1 | 66 | 124 | -3 | 37 | 46 | 2283 | 29 | 78 | -2286 |  | 129.4372
| 5 | 12 | Hurricane BI+ | 58 | 1 | PT:P2 | 66 | 124 | -3 | 37 | 46 | 2281 | 29 | 78 | -2284 |  | 129.4372
| 5 | 12 | Hurricane BI+ | 59 | 1 | PT:P3 | 66 | 123 | -3 | 37 | 46 | 2278 | 29 | 78 | -2281 |  | 128.4796
| 5 | 12 | Hurricane BI+ | 60 | 1 | PT:P4 | 66 | 123 | -3 | 37 | 46 | 2276 | 29 | 77 | -2279 |  | 128.4796
| 6 | 12 | Hurricane BI- | 1 | 1 | TL-S1 | 299 | -1280 | 0 | 164 | -634 | 4442 | 135 | -646 | -4441 |  | 1290.4635
| 6 | 12 | Hurricane BI- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 6 | 12 | Hurricane BI- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 6 | 12 | Hurricane BI- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 6 | 12 | Hurricane BI- | 10 | 1 | ST1 | 802 | -3852 | 6 | 421 | -1890 | 14236 | 381 | -1963 | -14230 |  | 3874.9427
| 6 | 12 | Hurricane BI- | 10 | 2 | ST2 | 802 | -3828 | 6 | 421 | -1878 | 14238 | 381 | -1950 | -14232 |  | 3851.0857
| 6 | 12 | Hurricane BI- | 10 | 3 | ST3 | 802 | -3802 | 6 | 421 | -1865 | 14239 | 381 | -1937 | -14233 |  | 3825.2426
| 6 | 12 | Hurricane BI- | 46 | 1 | F2 | 64 | -527 | 2 | 34 | -254 | 1216 | 30 | -273 | -1214 |  | 528.0994
| 6 | 12 | Hurricane BI- | 49 | 1 | S1 | 165 | -1278 | 2 | 90 | -626 | 4608 | 75 | -652 | -4605 |  | 1281.1667
| 6 | 12 | Hurricane BI- | 49 | 2 | S2 | 165 | -1275 | 2 | 90 | -625 | 4608 | 75 | -650 | -4606 |  | 1278.1741
| 6 | 12 | Hurricane BI- | 49 | 3 | S3 | 165 | -1272 | 2 | 90 | -624 | 4608 | 75 | -648 | -4606 |  | 1275.1816
| 6 | 12 | Hurricane BI- | 50 | 1 | S4 | 164 | -1235 | 2 | 90 | -604 | 4611 | 75 | -632 | -4608 |  | 1238.2766
| 6 | 12 | Hurricane BI- | 50 | 2 | S5 | 164 | -1231 | 2 | 90 | -602 | 4611 | 75 | -629 | -4608 |  | 1234.2872
| 6 | 12 | Hurricane BI- | 50 | 3 | S6 | 164 | -1227 | 2 | 90 | -600 | 4611 | 75 | -627 | -4609 |  | 1230.2979
| 6 | 12 | Hurricane BI- | 53 | 1 | S7 | 79 | -561 | 1 | 42 | -273 | 1613 | 37 | -288 | -1611 |  | 562.5709
| 6 | 12 | Hurricane BI- | 54 | 1 | S8 | 79 | -545 | 1 | 42 | -264 | 1615 | 37 | -281 | -1613 |  | 546.6169
| 6 | 12 | Hurricane BI- | 57 | 1 | PT:P1 | 66 | -924 | 3 | 37 | -446 | 2240 | 29 | -478 | -2237 |  | 924.7454
| 6 | 12 | Hurricane BI- | 58 | 1 | PT:P2 | 66 | -923 | 3 | 37 | -446 | 2237 | 29 | -478 | -2235 |  | 923.7462
| 6 | 12 | Hurricane BI- | 59 | 1 | PT:P3 | 66 | -922 | 3 | 37 | -445 | 2235 | 29 | -477 | -2232 |  | 922.747
| 6 | 12 | Hurricane BI- | 60 | 1 | PT:P4 | 66 | -921 | 3 | 37 | -445 | 2233 | 29 | -476 | -2230 |  | 921.7478
| 7 | 13 | NESC 250B NL+ | 1 | 1 | TL-S1 | 388 | -1014 | -3 | 212 | -519 | 6163 | 176 | -495 | -6166 |  | 1035.9291
| 7 | 13 | NESC 250B NL+ | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0 |  | 0
| 7 | 13 | NESC 250B NL+ | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 7 | 13 | NESC 250B NL+ | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 7 | 13 | NESC 250B NL+ | 10 | 1 | ST1 | 1082 | -2337 | -4 | 565 | -1189 | 19040 | 517 | -1148 | -19044 |  | 2404.3315
| 7 | 13 | NESC 250B NL+ | 10 | 2 | ST2 | 1082 | -2330 | -4 | 565 | -1185 | 19041 | 517 | -1145 | -19044 |  | 2397.5281
| 7 | 13 | NESC 250B NL+ | 10 | 3 | ST3 | 1082 | -2324 | -4 | 565 | -1181 | 19041 | 517 | -1142 | -19045 |  | 2391.6975
| 7 | 13 | NESC 250B NL+ | 46 | 1 | F2 | 85 | 103 | -1 | 43 | 46 | 824 | 42 | 58 | -825 |  | 111.6199
| 7 | 13 | NESC 250B NL+ | 49 | 1 | S1 | 225 | -795 | -2 | 122 | -407 | 6305 | 103 | -388 | -6307 |  | 804.309
| 7 | 13 | NESC 250B NL+ | 49 | 2 | S2 | 225 | -796 | -2 | 122 | -408 | 6305 | 103 | -388 | -6307 |  | 805.2975
| 7 | 13 | NESC 250B NL+ | 49 | 3 | S3 | 225 | -796 | -2 | 122 | -408 | 6305 | 103 | -389 | -6307 |  | 805.2975
| 7 | 13 | NESC 250B NL+ | 50 | 1 | S4 | 224 | -739 | -1 | 121 | -377 | 6307 | 103 | -362 | -6309 |  | 748.8411
| 7 | 13 | NESC 250B NL+ | 50 | 2 | S5 | 224 | -738 | -1 | 121 | -377 | 6307 | 103 | -361 | -6309 |  | 747.8543
| 7 | 13 | NESC 250B NL+ | 50 | 3 | S6 | 224 | -738 | -1 | 121 | -377 | 6307 | 103 | -361 | -6309 |  | 747.8543
| 7 | 13 | NESC 250B NL+ | 53 | 1 | S7 | 104 | -47 | -1 | 53 | -29 | 1469 | 51 | -18 | -1471 |  | 70.8449
| 7 | 13 | NESC 250B NL+ | 54 | 1 | S8 | 104 | -32 | -1 | 53 | -21 | 1470 | 51 | -11 | -1471 |  | 61.9193
| 7 | 13 | NESC 250B NL+ | 57 | 1 | PT:P1 | 80 | 155 | -2 | 42 | 67 | 1616 | 38 | 89 | -1618 |  | 160.602
| 7 | 13 | NESC 250B NL+ | 58 | 1 | PT:P2 | 80 | 155 | -2 | 42 | 67 | 1616 | 38 | 89 | -1618 |  | 160.602
| 7 | 13 | NESC 250B NL+ | 59 | 1 | PT:P3 | 80 | 155 | -2 | 42 | 67 | 1616 | 38 | 89 | -1618 |  | 160.602
| 7 | 13 | NESC 250B NL+ | 60 | 1 | PT:P4 | 80 | 155 | -2 | 42 | 67 | 1616 | 38 | 89 | -1618 |  | 160.602
| 8 | 13 | NESC 250B NL- | 1 | 1 | TL-S1 | 388 | -1527 | -1 | 212 | -764 | 6138 | 176 | -764 | -6139 |  | 1541.6465
| 8 | 13 | NESC 250B NL- | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 8 | 13 | NESC 250B NL- | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 8 | 13 | NESC 250B NL- | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 8 | 13 | NESC 250B NL- | 10 | 1 | ST1 | 1082 | -4280 | 4 | 565 | -2117 | 18969 | 517 | -2163 | -18965 |  | 4317.1334
| 8 | 13 | NESC 250B NL- | 10 | 2 | ST2 | 1082 | -4273 | 4 | 565 | -2113 | 18970 | 517 | -2160 | -18966 |  | 4310.1937
| 8 | 13 | NESC 250B NL- | 10 | 3 | ST3 | 1082 | -4266 | 4 | 565 | -2110 | 18970 | 517 | -2157 | -18966 |  | 4303.2542
| 8 | 13 | NESC 250B NL- | 46 | 1 | F2 | 85 | -385 | 1 | 43 | -186 | 804 | 42 | -199 | -803 |  | 387.3951
| 8 | 13 | NESC 250B NL- | 49 | 1 | S1 | 225 | -1489 | 1 | 122 | -737 | 6275 | 103 | -752 | -6274 |  | 1493.99
| 8 | 13 | NESC 250B NL- | 49 | 2 | S2 | 225 | -1490 | 1 | 122 | -737 | 6275 | 103 | -753 | -6274 |  | 1494.9866
| 8 | 13 | NESC 250B NL- | 49 | 3 | S3 | 225 | -1490 | 1 | 122 | -737 | 6275 | 103 | -753 | -6274 |  | 1494.9866
| 8 | 13 | NESC 250B NL- | 50 | 1 | S4 | 224 | -1431 | 2 | 121 | -706 | 6279 | 103 | -725 | -6277 |  | 1436.1079
| 8 | 13 | NESC 250B NL- | 50 | 2 | S5 | 224 | -1430 | 2 | 121 | -706 | 6279 | 103 | -725 | -6277 |  | 1435.1115
| 8 | 13 | NESC 250B NL- | 50 | 3 | S6 | 224 | -1430 | 2 | 121 | -705 | 6279 | 103 | -725 | -6277 |  | 1435.1115
| 8 | 13 | NESC 250B NL- | 53 | 1 | S7 | 104 | -485 | 1 | 53 | -237 | 1451 | 51 | -248 | -1450 |  | 487.8883
| 8 | 13 | NESC 250B NL- | 54 | 1 | S8 | 104 | -470 | 1 | 53 | -229 | 1452 | 51 | -241 | -1451 |  | 472.9799
| 8 | 13 | NESC 250B NL- | 57 | 1 | PT:P1 | 80 | -721 | 2 | 42 | -349 | 1579 | 38 | -372 | -1577 |  | 722.225
| 8 | 13 | NESC 250B NL- | 58 | 1 | PT:P2 | 80 | -721 | 2 | 42 | -349 | 1579 | 38 | -372 | -1577 |  | 722.225
| 8 | 13 | NESC 250B NL- | 59 | 1 | PT:P3 | 80 | -721 | 2 | 42 | -349 | 1579 | 38 | -372 | -1577 |  | 722.225
| 8 | 13 | NESC 250B NL- | 60 | 1 | PT:P4 | 80 | -721 | 2 | 42 | -349 | 1579 | 38 | -372 | -1577 |  | 722.225
| 9 | 13 | NESC 250B NR+ | 1 | 1 | TL-S1 | 388 | -1013 | -4 | 212 | -523 | 6163 | 176 | -490 | -6166 |  | 1034.9536
| 9 | 13 | NESC 250B NR+ | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 9 | 13 | NESC 250B NR+ | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 9 | 13 | NESC 250B NR+ | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 9 | 13 | NESC 250B NR+ | 10 | 1 | ST1 | 1082 | -2335 | -6 | 565 | -1201 | 19039 | 517 | -1134 | -19045 |  | 2402.3917
| 9 | 13 | NESC 250B NR+ | 10 | 2 | ST2 | 1082 | -2329 | -6 | 565 | -1197 | 19040 | 517 | -1131 | -19046 |  | 2396.5605
| 9 | 13 | NESC 250B NR+ | 10 | 3 | ST3 | 1082 | -2322 | -6 | 565 | -1194 | 19040 | 517 | -1128 | -19046 |  | 2389.7584
| 9 | 13 | NESC 250B NR+ | 46 | 1 | F2 | 85 | 104 | -2 | 43 | 42 | 824 | 42 | 62 | -825 |  | 112.5567
| 9 | 13 | NESC 250B NR+ | 49 | 1 | S1 | 225 | -794 | -3 | 121 | -412 | 6305 | 103 | -382 | -6308 |  | 803.1725
| 9 | 13 | NESC 250B NR+ | 49 | 2 | S2 | 225 | -795 | -3 | 121 | -413 | 6305 | 103 | -382 | -6308 |  | 804.1611
| 9 | 13 | NESC 250B NR+ | 49 | 3 | S3 | 225 | -796 | -3 | 121 | -413 | 6305 | 103 | -383 | -6308 |  | 805.1497
| 9 | 13 | NESC 250B NR+ | 50 | 1 | S4 | 224 | -738 | -2 | 121 | -382 | 6307 | 103 | -356 | -6309 |  | 747.8563
| 9 | 13 | NESC 250B NR+ | 50 | 2 | S5 | 224 | -738 | -2 | 121 | -382 | 6307 | 103 | -356 | -6309 |  | 747.8563
| 9 | 13 | NESC 250B NR+ | 50 | 3 | S6 | 224 | -737 | -2 | 121 | -382 | 6307 | 103 | -355 | -6309 |  | 746.8695
| 9 | 13 | NESC 250B NR+ | 53 | 1 | S7 | 104 | -46 | -2 | 53 | -32 | 1469 | 51 | -14 | -1471 |  | 70.2068
| 9 | 13 | NESC 250B NR+ | 54 | 1 | S8 | 104 | -32 | -2 | 53 | -24 | 1469 | 51 | -7 | -1471 |  | 61.9435
| 9 | 13 | NESC 250B NR+ | 57 | 1 | PT:P1 | 80 | 156 | -3 | 42 | 60 | 1616 | 38 | 96 | -1619 |  | 161.5828
| 9 | 13 | NESC 250B NR+ | 58 | 1 | PT:P2 | 80 | 156 | -3 | 42 | 60 | 1616 | 38 | 96 | -1619 |  | 161.5828
| 9 | 13 | NESC 250B NR+ | 59 | 1 | PT:P3 | 80 | 156 | -3 | 42 | 60 | 1616 | 38 | 96 | -1619 |  | 161.5828
| 9 | 13 | NESC 250B NR+ | 60 | 1 | PT:P4 | 80 | 156 | -3 | 42 | 60 | 1616 | 38 | 96 | -1619 |  | 161.5828
| 10 | 13 | NESC 250B NR- | 1 | 1 | TL-S1 | 388 | -1528 | 0 | 212 | -759 | 6139 | 176 | -769 | -6139 |  | 1542.6367
| 10 | 13 | NESC 250B NR- | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 10 | 13 | NESC 250B NR- | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 10 | 13 | NESC 250B NR- | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 10 | 13 | NESC 250B NR- | 10 | 1 | ST1 | 1082 | -4282 | 6 | 565 | -2104 | 18970 | 517 | -2177 | -18964 |  | 4319.1185
| 10 | 13 | NESC 250B NR- | 10 | 2 | ST2 | 1082 | -4275 | 6 | 565 | -2101 | 18971 | 517 | -2174 | -18965 |  | 4312.1788
| 10 | 13 | NESC 250B NR- | 10 | 3 | ST3 | 1082 | -4268 | 6 | 565 | -2097 | 18971 | 517 | -2171 | -18965 |  | 4305.2393
| 10 | 13 | NESC 250B NR- | 46 | 1 | F2 | 85 | -385 | 2 | 43 | -182 | 804 | 42 | -203 | -802 |  | 387.399
| 10 | 13 | NESC 250B NR- | 49 | 1 | S1 | 225 | -1490 | 2 | 121 | -731 | 6276 | 103 | -758 | -6273 |  | 1494.9064
| 10 | 13 | NESC 250B NR- | 49 | 2 | S2 | 225 | -1490 | 2 | 121 | -732 | 6276 | 103 | -759 | -6273 |  | 1494.9064
| 10 | 13 | NESC 250B NR- | 49 | 3 | S3 | 225 | -1491 | 2 | 121 | -732 | 6276 | 103 | -759 | -6273 |  | 1495.9031
| 10 | 13 | NESC 250B NR- | 50 | 1 | S4 | 224 | -1432 | 3 | 121 | -701 | 6279 | 103 | -731 | -6277 |  | 1437.1061
| 10 | 13 | NESC 250B NR- | 50 | 2 | S5 | 224 | -1431 | 3 | 121 | -701 | 6279 | 103 | -731 | -6277 |  | 1436.1097
| 10 | 13 | NESC 250B NR- | 50 | 3 | S6 | 224 | -1431 | 3 | 121 | -700 | 6279 | 103 | -730 | -6277 |  | 1436.1097
| 10 | 13 | NESC 250B NR- | 53 | 1 | S7 | 104 | -485 | 2 | 53 | -234 | 1451 | 51 | -252 | -1449 |  | 487.8914
| 10 | 13 | NESC 250B NR- | 54 | 1 | S8 | 104 | -471 | 2 | 53 | -226 | 1452 | 51 | -244 | -1450 |  | 473.9768
| 10 | 13 | NESC 250B NR- | 57 | 1 | PT:P1 | 80 | -722 | 3 | 42 | -343 | 1580 | 38 | -379 | -1577 |  | 723.2268
| 10 | 13 | NESC 250B NR- | 58 | 1 | PT:P2 | 80 | -722 | 3 | 42 | -343 | 1580 | 38 | -379 | -1577 |  | 723.2268
| 10 | 13 | NESC 250B NR- | 59 | 1 | PT:P3 | 80 | -722 | 3 | 42 | -343 | 1580 | 38 | -379 | -1577 |  | 723.2268
| 10 | 13 | NESC 250B NR- | 60 | 1 | PT:P4 | 80 | -722 | 3 | 42 | -343 | 1580 | 38 | -379 | -1577 |  | 723.2268
| 11 | 13 | NESC 250B BI+ | 1 | 1 | TL-S1 | 388 | -1012 | -3 | 212 | -520 | 6163 | 176 | -492 | -6166 |  | 1033.9715
| 11 | 13 | NESC 250B BI+ | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 11 | 13 | NESC 250B BI+ | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 11 | 13 | NESC 250B BI+ | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 11 | 13 | NESC 250B BI+ | 10 | 1 | ST1 | 1082 | -2329 | -5 | 565 | -1192 | 19040 | 517 | -1138 | -19045 |  | 2396.5582
| 11 | 13 | NESC 250B BI+ | 10 | 2 | ST2 | 1082 | -2322 | -5 | 565 | -1188 | 19040 | 517 | -1134 | -19045 |  | 2389.7561
| 11 | 13 | NESC 250B BI+ | 10 | 3 | ST3 | 1082 | -2316 | -5 | 565 | -1184 | 19041 | 517 | -1131 | -19045 |  | 2383.9266
| 11 | 13 | NESC 250B BI+ | 46 | 1 | F2 | 85 | 105 | -1 | 43 | 45 | 824 | 42 | 61 | -826 |  | 113.4681
| 11 | 13 | NESC 250B BI+ | 49 | 1 | S1 | 225 | -792 | -2 | 122 | -409 | 6305 | 103 | -383 | -6307 |  | 801.3439
| 11 | 13 | NESC 250B BI+ | 49 | 2 | S2 | 225 | -793 | -2 | 122 | -409 | 6305 | 103 | -384 | -6307 |  | 802.3322
| 11 | 13 | NESC 250B BI+ | 49 | 3 | S3 | 225 | -793 | -2 | 122 | -409 | 6305 | 103 | -384 | -6307 |  | 802.3322
| 11 | 13 | NESC 250B BI+ | 50 | 1 | S4 | 224 | -736 | -2 | 121 | -379 | 6307 | 103 | -357 | -6309 |  | 745.8827
| 11 | 13 | NESC 250B BI+ | 50 | 2 | S5 | 224 | -735 | -2 | 121 | -378 | 6307 | 103 | -357 | -6309 |  | 744.896
| 11 | 13 | NESC 250B BI+ | 50 | 3 | S6 | 224 | -735 | -2 | 121 | -378 | 6307 | 103 | -357 | -6309 |  | 744.896
| 11 | 13 | NESC 250B BI+ | 53 | 1 | S7 | 104 | -45 | -1 | 53 | -30 | 1469 | 51 | -15 | -1471 |  | 69.5342
| 11 | 13 | NESC 250B BI+ | 54 | 1 | S8 | 104 | -30 | -1 | 53 | -22 | 1470 | 51 | -8 | -1472 |  | 60.9098
| 11 | 13 | NESC 250B BI+ | 57 | 1 | PT:P1 | 80 | 159 | -3 | 42 | 65 | 1616 | 38 | 94 | -1619 |  | 164.481
| 11 | 13 | NESC 250B BI+ | 58 | 1 | PT:P2 | 80 | 159 | -3 | 42 | 65 | 1616 | 38 | 94 | -1619 |  | 164.481
| 11 | 13 | NESC 250B BI+ | 59 | 1 | PT:P3 | 80 | 159 | -3 | 42 | 65 | 1616 | 38 | 94 | -1619 |  | 164.481
| 11 | 13 | NESC 250B BI+ | 60 | 1 | PT:P4 | 80 | 159 | -3 | 42 | 65 | 1616 | 38 | 94 | -1619 |  | 164.481
| 12 | 13 | NESC 250B BI- | 1 | 1 | TL-S1 | 388 | -1530 | 0 | 212 | -762 | 6138 | 176 | -767 | -6139 |  | 1544.6178
| 12 | 13 | NESC 250B BI- | 9 | 1 | T1 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 12 | 13 | NESC 250B BI- | 9 | 2 | T2 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 12 | 13 | NESC 250B BI- | 9 | 3 | T3 | 131 | 0 | 0 | 0 | 0 | 0 | 131 | 0 | 0
| 12 | 13 | NESC 250B BI- | 10 | 1 | ST1 | 1082 | -4288 | 5 | 565 | -2114 | 18970 | 517 | -2174 | -18965 |  | 4325.0658
| 12 | 13 | NESC 250B BI- | 10 | 2 | ST2 | 1082 | -4281 | 5 | 565 | -2110 | 18970 | 517 | -2171 | -18965 |  | 4318.1259
| 12 | 13 | NESC 250B BI- | 10 | 3 | ST3 | 1082 | -4275 | 5 | 565 | -2107 | 18970 | 517 | -2168 | -18965 |  | 4312.1775
| 12 | 13 | NESC 250B BI- | 46 | 1 | F2 | 85 | -387 | 1 | 43 | -185 | 804 | 42 | -202 | -803 |  | 389.3828
| 12 | 13 | NESC 250B BI- | 49 | 1 | S1 | 225 | -1492 | 2 | 122 | -735 | 6275 | 103 | -757 | -6274 |  | 1496.981
| 12 | 13 | NESC 250B BI- | 49 | 2 | S2 | 225 | -1493 | 2 | 122 | -736 | 6275 | 103 | -757 | -6274 |  | 1497.9776
| 12 | 13 | NESC 250B BI- | 49 | 3 | S3 | 225 | -1494 | 2 | 122 | -736 | 6275 | 103 | -757 | -6274 |  | 1498.9743
| 12 | 13 | NESC 250B BI- | 50 | 1 | S4 | 224 | -1434 | 2 | 121 | -705 | 6279 | 103 | -730 | -6277 |  | 1439.0973
| 12 | 13 | NESC 250B BI- | 50 | 2 | S5 | 224 | -1434 | 2 | 121 | -704 | 6279 | 103 | -729 | -6277 |  | 1439.0973
| 12 | 13 | NESC 250B BI- | 50 | 3 | S6 | 224 | -1433 | 2 | 121 | -704 | 6279 | 103 | -729 | -6277 |  | 1438.1008
| 12 | 13 | NESC 250B BI- | 53 | 1 | S7 | 104 | -487 | 1 | 53 | -236 | 1451 | 51 | -251 | -1449 |  | 489.8765
| 12 | 13 | NESC 250B BI- | 54 | 1 | S8 | 104 | -472 | 1 | 53 | -229 | 1453 | 51 | -244 | -1451 |  | 474.9674
| 12 | 13 | NESC 250B BI- | 57 | 1 | PT:P1 | 80 | -725 | 3 | 42 | -348 | 1579 | 38 | -377 | -1577 |  | 726.2217
| 12 | 13 | NESC 250B BI- | 58 | 1 | PT:P2 | 80 | -725 | 3 | 42 | -348 | 1579 | 38 | -377 | -1577 |  | 726.2217
| 12 | 13 | NESC 250B BI- | 59 | 1 | PT:P3 | 80 | -725 | 3 | 42 | -348 | 1579 | 38 | -377 | -1577 |  | 726.2217
| 12 | 13 | NESC 250B BI- | 60 | 1 | PT:P4 | 80 | -725 | 3 | 42 | -348 | 1579 | 38 | -377 | -1577 |  | 726.2217
| 13 | 16 | Rule 250D NL+ | 1 | 1 | TL-S1 | 449 | -815 | -1 | 235 | -413 | 4267 | 214 | -402 | -4268 |  | 848.2046
| 13 | 16 | Rule 250D NL+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 13 | 16 | Rule 250D NL+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 13 | 16 | Rule 250D NL+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 13 | 16 | Rule 250D NL+ | 10 | 1 | ST1 | 1175 | -2180 | -1 | 597 | -1093 | 13556 | 578 | -1087 | -13557 |  | 2260.2677
| 13 | 16 | Rule 250D NL+ | 10 | 2 | ST2 | 1175 | -2175 | -1 | 597 | -1091 | 13557 | 578 | -1085 | -13557 |  | 2255.4456
| 13 | 16 | Rule 250D NL+ | 10 | 3 | ST3 | 1175 | -2170 | -1 | 597 | -1088 | 13557 | 578 | -1082 | -13557 |  | 2250.6244
| 13 | 16 | Rule 250D NL+ | 46 | 1 | F2 | 207 | -66 | 0 | 100 | -35 | 762 | 107 | -32 | -762 |  | 119.8165
| 13 | 16 | Rule 250D NL+ | 49 | 1 | S1 | 338 | -749 | 0 | 171 | -377 | 4544 | 166 | -372 | -4545 |  | 768.2721
| 13 | 16 | Rule 250D NL+ | 49 | 2 | S2 | 338 | -749 | 0 | 171 | -377 | 4544 | 166 | -372 | -4544 |  | 768.2721
| 13 | 16 | Rule 250D NL+ | 49 | 3 | S3 | 338 | -750 | 0 | 171 | -378 | 4544 | 166 | -372 | -4544 |  | 769.247
| 13 | 16 | Rule 250D NL+ | 50 | 1 | S4 | 336 | -708 | 0 | 171 | -355 | 4546 | 166 | -353 | -4546 |  | 728.3577
| 13 | 16 | Rule 250D NL+ | 50 | 2 | S5 | 336 | -708 | 0 | 171 | -355 | 4546 | 166 | -353 | -4546 |  | 728.3577
| 13 | 16 | Rule 250D NL+ | 50 | 3 | S6 | 336 | -707 | 0 | 171 | -355 | 4546 | 166 | -352 | -4546 |  | 727.3857
| 13 | 16 | Rule 250D NL+ | 53 | 1 | S7 | 214 | -193 | 0 | 105 | -98 | 1402 | 109 | -94 | -1402 |  | 219.7134
| 13 | 16 | Rule 250D NL+ | 54 | 1 | S8 | 213 | -178 | 0 | 104 | -91 | 1403 | 109 | -88 | -1403 |  | 206.1553
| 13 | 16 | Rule 250D NL+ | 57 | 1 | PT:P1 | 270 | -146 | 0 | 130 | -75 | 1305 | 140 | -71 | -1306 |  | 195.4891
| 13 | 16 | Rule 250D NL+ | 58 | 1 | PT:P2 | 270 | -146 | 0 | 130 | -75 | 1305 | 140 | -71 | -1306 |  | 195.4891
| 13 | 16 | Rule 250D NL+ | 59 | 1 | PT:P3 | 270 | -146 | 0 | 130 | -75 | 1305 | 140 | -71 | -1306 |  | 195.4891
| 13 | 16 | Rule 250D NL+ | 60 | 1 | PT:P4 | 270 | -146 | 0 | 130 | -75 | 1305 | 140 | -71 | -1306 |  | 195.4891
| 14 | 16 | Rule 250D NL- | 1 | 1 | TL-S1 | 449 | -947 | -1 | 235 | -476 | 4261 | 214 | -471 | -4261 |  | 975.7228
| 14 | 16 | Rule 250D NL- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 14 | 16 | Rule 250D NL- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 14 | 16 | Rule 250D NL- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 14 | 16 | Rule 250D NL- | 10 | 1 | ST1 | 1175 | -2538 | 1 | 597 | -1264 | 13543 | 578 | -1274 | -13542 |  | 2607.2695
| 14 | 16 | Rule 250D NL- | 10 | 2 | ST2 | 1175 | -2533 | 1 | 597 | -1261 | 13543 | 578 | -1272 | -13542 |  | 2602.4025
| 14 | 16 | Rule 250D NL- | 10 | 3 | ST3 | 1175 | -2528 | 1 | 597 | -1258 | 13543 | 578 | -1270 | -13542 |  | 2597.5361
| 14 | 16 | Rule 250D NL- | 46 | 1 | F2 | 207 | -196 | 0 | 100 | -96 | 757 | 107 | -100 | -756 |  | 220.0364
| 14 | 16 | Rule 250D NL- | 49 | 1 | S1 | 338 | -900 | 0 | 171 | -449 | 4538 | 166 | -451 | -4537 |  | 916.101
| 14 | 16 | Rule 250D NL- | 49 | 2 | S2 | 338 | -900 | 0 | 171 | -449 | 4538 | 166 | -451 | -4537 |  | 916.101
| 14 | 16 | Rule 250D NL- | 49 | 3 | S3 | 338 | -901 | 0 | 171 | -449 | 4537 | 166 | -452 | -4537 |  | 917.0834
| 14 | 16 | Rule 250D NL- | 50 | 1 | S4 | 336 | -859 | 0 | 171 | -427 | 4540 | 166 | -432 | -4539 |  | 875.855
| 14 | 16 | Rule 250D NL- | 50 | 2 | S5 | 336 | -858 | 0 | 171 | -426 | 4540 | 166 | -432 | -4539 |  | 874.8743
| 14 | 16 | Rule 250D NL- | 50 | 3 | S6 | 336 | -858 | 0 | 171 | -426 | 4540 | 166 | -431 | -4539 |  | 874.8743
| 14 | 16 | Rule 250D NL- | 53 | 1 | S7 | 214 | -317 | 0 | 105 | -157 | 1397 | 109 | -160 | -1396 |  | 333.9371
| 14 | 16 | Rule 250D NL- | 54 | 1 | S8 | 213 | -303 | 0 | 104 | -150 | 1397 | 109 | -153 | -1397 |  | 320.3514
| 14 | 16 | Rule 250D NL- | 57 | 1 | PT:P1 | 270 | -315 | 0 | 130 | -155 | 1298 | 140 | -160 | -1298 |  | 340.7712
| 14 | 16 | Rule 250D NL- | 58 | 1 | PT:P2 | 270 | -315 | 0 | 130 | -155 | 1298 | 140 | -160 | -1298 |  | 340.7712
| 14 | 16 | Rule 250D NL- | 59 | 1 | PT:P3 | 270 | -315 | 0 | 130 | -155 | 1298 | 140 | -160 | -1298 |  | 340.7712
| 14 | 16 | Rule 250D NL- | 60 | 1 | PT:P4 | 270 | -315 | 0 | 130 | -155 | 1298 | 140 | -160 | -1298 |  | 340.7712
| 15 | 16 | Rule 250D NR+ | 1 | 1 | TL-S1 | 449 | -815 | -1 | 235 | -414 | 4267 | 214 | -400 | -4268 |  | 848.2046
| 15 | 16 | Rule 250D NR+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 15 | 16 | Rule 250D NR+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 15 | 16 | Rule 250D NR+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 15 | 16 | Rule 250D NR+ | 10 | 1 | ST1 | 1175 | -2180 | -1 | 597 | -1095 | 13556 | 578 | -1084 | -13557 |  | 2260.2677
| 15 | 16 | Rule 250D NR+ | 10 | 2 | ST2 | 1175 | -2175 | -1 | 597 | -1093 | 13556 | 578 | -1082 | -13557 |  | 2255.4456
| 15 | 16 | Rule 250D NR+ | 10 | 3 | ST3 | 1175 | -2170 | -1 | 597 | -1090 | 13557 | 578 | -1080 | -13558 |  | 2250.6244
| 15 | 16 | Rule 250D NR+ | 46 | 1 | F2 | 207 | -66 | 0 | 100 | -36 | 762 | 107 | -31 | -762 |  | 119.8165
| 15 | 16 | Rule 250D NR+ | 49 | 1 | S1 | 338 | -749 | -1 | 171 | -378 | 4544 | 166 | -371 | -4545 |  | 768.2727
| 15 | 16 | Rule 250D NR+ | 49 | 2 | S2 | 338 | -749 | -1 | 171 | -378 | 4544 | 166 | -371 | -4545 |  | 768.2727
| 15 | 16 | Rule 250D NR+ | 49 | 3 | S3 | 338 | -750 | -1 | 171 | -379 | 4544 | 166 | -371 | -4545 |  | 769.2477
| 15 | 16 | Rule 250D NR+ | 50 | 1 | S4 | 336 | -708 | 0 | 171 | -356 | 4546 | 166 | -352 | -4546 |  | 728.3577
| 15 | 16 | Rule 250D NR+ | 50 | 2 | S5 | 336 | -707 | 0 | 171 | -356 | 4546 | 166 | -351 | -4546 |  | 727.3857
| 15 | 16 | Rule 250D NR+ | 50 | 3 | S6 | 336 | -707 | 0 | 171 | -356 | 4546 | 166 | -351 | -4546 |  | 727.3857
| 15 | 16 | Rule 250D NR+ | 53 | 1 | S7 | 214 | -192 | -1 | 105 | -99 | 1402 | 109 | -93 | -1402 |  | 218.8378
| 15 | 16 | Rule 250D NR+ | 54 | 1 | S8 | 213 | -178 | 0 | 104 | -91 | 1402 | 109 | -87 | -1403 |  | 206.1553
| 15 | 16 | Rule 250D NR+ | 57 | 1 | PT:P1 | 270 | -145 | -1 | 130 | -76 | 1305 | 140 | -69 | -1306 |  | 194.746
| 15 | 16 | Rule 250D NR+ | 58 | 1 | PT:P2 | 270 | -145 | -1 | 130 | -76 | 1305 | 140 | -69 | -1306 |  | 194.746
| 15 | 16 | Rule 250D NR+ | 59 | 1 | PT:P3 | 270 | -145 | -1 | 130 | -76 | 1305 | 140 | -69 | -1306 |  | 194.746
| 15 | 16 | Rule 250D NR+ | 60 | 1 | PT:P4 | 270 | -145 | -1 | 130 | -76 | 1305 | 140 | -69 | -1306 |  | 194.746
| 16 | 16 | Rule 250D NR- | 1 | 1 | TL-S1 | 449 | -947 | 0 | 235 | -475 | 4261 | 214 | -472 | -4261 |  | 975.7223
| 16 | 16 | Rule 250D NR- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 16 | 16 | Rule 250D NR- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 16 | 16 | Rule 250D NR- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 16 | 16 | Rule 250D NR- | 10 | 1 | ST1 | 1175 | -2538 | 1 | 597 | -1261 | 13543 | 578 | -1277 | -13541 |  | 2607.2695
| 16 | 16 | Rule 250D NR- | 10 | 2 | ST2 | 1175 | -2533 | 1 | 597 | -1259 | 13543 | 578 | -1275 | -13542 |  | 2602.4025
| 16 | 16 | Rule 250D NR- | 10 | 3 | ST3 | 1175 | -2528 | 1 | 597 | -1256 | 13543 | 578 | -1272 | -13542 |  | 2597.5361
| 16 | 16 | Rule 250D NR- | 46 | 1 | F2 | 207 | -196 | 0 | 100 | -95 | 757 | 107 | -101 | -756 |  | 220.0364
| 16 | 16 | Rule 250D NR- | 49 | 1 | S1 | 338 | -900 | 0 | 171 | -448 | 4538 | 166 | -452 | -4537 |  | 916.101
| 16 | 16 | Rule 250D NR- | 49 | 2 | S2 | 338 | -900 | 0 | 171 | -448 | 4538 | 166 | -453 | -4537 |  | 916.101
| 16 | 16 | Rule 250D NR- | 49 | 3 | S3 | 338 | -901 | 0 | 171 | -448 | 4538 | 166 | -453 | -4537 |  | 917.0834
| 16 | 16 | Rule 250D NR- | 50 | 1 | S4 | 336 | -859 | 1 | 171 | -426 | 4540 | 166 | -433 | -4539 |  | 875.8556
| 16 | 16 | Rule 250D NR- | 50 | 2 | S5 | 336 | -858 | 1 | 171 | -425 | 4540 | 166 | -433 | -4539 |  | 874.8748
| 16 | 16 | Rule 250D NR- | 50 | 3 | S6 | 336 | -858 | 1 | 171 | -425 | 4540 | 166 | -433 | -4539 |  | 874.8748
| 16 | 16 | Rule 250D NR- | 53 | 1 | S7 | 214 | -317 | 0 | 105 | -156 | 1397 | 109 | -161 | -1396 |  | 333.9371
| 16 | 16 | Rule 250D NR- | 54 | 1 | S8 | 213 | -303 | 0 | 104 | -149 | 1398 | 109 | -154 | -1397 |  | 320.3514
| 16 | 16 | Rule 250D NR- | 57 | 1 | PT:P1 | 270 | -315 | 1 | 130 | -154 | 1298 | 140 | -161 | -1298 |  | 340.7727
| 16 | 16 | Rule 250D NR- | 58 | 1 | PT:P2 | 270 | -315 | 1 | 130 | -154 | 1298 | 140 | -161 | -1298 |  | 340.7727
| 16 | 16 | Rule 250D NR- | 59 | 1 | PT:P3 | 270 | -315 | 1 | 130 | -154 | 1298 | 140 | -161 | -1298 |  | 340.7727
| 16 | 16 | Rule 250D NR- | 60 | 1 | PT:P4 | 270 | -315 | 1 | 130 | -154 | 1298 | 140 | -161 | -1298 |  | 340.7727
| 17 | 16 | Rule 250D BI+ | 1 | 1 | TL-S1 | 449 | -814 | -1 | 235 | -413 | 4267 | 214 | -401 | -4268 |  | 847.2438
| 17 | 16 | Rule 250D BI+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 17 | 16 | Rule 250D BI+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 17 | 16 | Rule 250D BI+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 17 | 16 | Rule 250D BI+ | 10 | 1 | ST1 | 1175 | -2178 | -1 | 597 | -1094 | 13556 | 578 | -1085 | -13557 |  | 2258.3388
| 17 | 16 | Rule 250D BI+ | 10 | 2 | ST2 | 1175 | -2174 | -1 | 597 | -1091 | 13557 | 578 | -1082 | -13557 |  | 2254.4813
| 17 | 16 | Rule 250D BI+ | 10 | 3 | ST3 | 1175 | -2169 | -1 | 597 | -1089 | 13557 | 578 | -1080 | -13557 |  | 2249.6602
| 17 | 16 | Rule 250D BI+ | 46 | 1 | F2 | 207 | -66 | 0 | 100 | -35 | 762 | 107 | -31 | -762 |  | 119.8165
| 17 | 16 | Rule 250D BI+ | 49 | 1 | S1 | 338 | -748 | -1 | 171 | -377 | 4544 | 166 | -371 | -4545 |  | 767.2979
| 17 | 16 | Rule 250D BI+ | 49 | 2 | S2 | 338 | -749 | -1 | 171 | -378 | 4544 | 166 | -371 | -4545 |  | 768.2727
| 17 | 16 | Rule 250D BI+ | 49 | 3 | S3 | 338 | -749 | -1 | 171 | -378 | 4544 | 166 | -371 | -4545 |  | 768.2727
| 17 | 16 | Rule 250D BI+ | 50 | 1 | S4 | 336 | -707 | 0 | 171 | -356 | 4546 | 166 | -352 | -4546 |  | 727.3857
| 17 | 16 | Rule 250D BI+ | 50 | 2 | S5 | 336 | -707 | 0 | 171 | -355 | 4546 | 166 | -352 | -4546 |  | 727.3857
| 17 | 16 | Rule 250D BI+ | 50 | 3 | S6 | 336 | -706 | 0 | 171 | -355 | 4546 | 166 | -351 | -4546 |  | 726.4138
| 17 | 16 | Rule 250D BI+ | 53 | 1 | S7 | 214 | -192 | 0 | 105 | -98 | 1402 | 109 | -94 | -1402 |  | 218.8356
| 17 | 16 | Rule 250D BI+ | 54 | 1 | S8 | 213 | -178 | 0 | 104 | -91 | 1402 | 109 | -87 | -1403 |  | 206.1553
| 17 | 16 | Rule 250D BI+ | 57 | 1 | PT:P1 | 270 | -145 | -1 | 130 | -75 | 1305 | 140 | -70 | -1306 |  | 194.746
| 17 | 16 | Rule 250D BI+ | 58 | 1 | PT:P2 | 270 | -145 | -1 | 130 | -75 | 1305 | 140 | -70 | -1306 |  | 194.746
| 17 | 16 | Rule 250D BI+ | 59 | 1 | PT:P3 | 270 | -145 | -1 | 130 | -75 | 1305 | 140 | -70 | -1306 |  | 194.746
| 17 | 16 | Rule 250D BI+ | 60 | 1 | PT:P4 | 270 | -145 | -1 | 130 | -75 | 1305 | 140 | -70 | -1306 |  | 194.746
| 18 | 16 | Rule 250D BI- | 1 | 1 | TL-S1 | 449 | -947 | -1 | 235 | -476 | 4261 | 214 | -472 | -4261 |  | 975.7228
| 18 | 16 | Rule 250D BI- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 18 | 16 | Rule 250D BI- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 18 | 16 | Rule 250D BI- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 18 | 16 | Rule 250D BI- | 10 | 1 | ST1 | 1175 | -2539 | 1 | 597 | -1263 | 13543 | 578 | -1276 | -13541 |  | 2608.2429
| 18 | 16 | Rule 250D BI- | 10 | 2 | ST2 | 1175 | -2534 | 1 | 597 | -1260 | 13543 | 578 | -1274 | -13542 |  | 2603.3759
| 18 | 16 | Rule 250D BI- | 10 | 3 | ST3 | 1175 | -2530 | 1 | 597 | -1258 | 13543 | 578 | -1272 | -13542 |  | 2599.4826
| 18 | 16 | Rule 250D BI- | 46 | 1 | F2 | 207 | -197 | 0 | 100 | -96 | 757 | 107 | -101 | -756 |  | 220.9276
| 18 | 16 | Rule 250D BI- | 49 | 1 | S1 | 338 | -900 | 0 | 171 | -448 | 4538 | 166 | -452 | -4537 |  | 916.101
| 18 | 16 | Rule 250D BI- | 49 | 2 | S2 | 338 | -901 | 0 | 171 | -449 | 4538 | 166 | -452 | -4537 |  | 917.0834
| 18 | 16 | Rule 250D BI- | 49 | 3 | S3 | 338 | -902 | 0 | 171 | -449 | 4538 | 166 | -453 | -4537 |  | 918.0659
| 18 | 16 | Rule 250D BI- | 50 | 1 | S4 | 336 | -859 | 1 | 171 | -426 | 4540 | 166 | -433 | -4539 |  | 875.8556
| 18 | 16 | Rule 250D BI- | 50 | 2 | S5 | 336 | -859 | 1 | 171 | -426 | 4540 | 166 | -433 | -4539 |  | 875.8556
| 18 | 16 | Rule 250D BI- | 50 | 3 | S6 | 336 | -858 | 1 | 171 | -426 | 4540 | 166 | -432 | -4539 |  | 874.8748
| 18 | 16 | Rule 250D BI- | 53 | 1 | S7 | 214 | -318 | 0 | 105 | -157 | 1397 | 109 | -161 | -1396 |  | 334.8865
| 18 | 16 | Rule 250D BI- | 54 | 1 | S8 | 213 | -303 | 0 | 104 | -149 | 1397 | 109 | -154 | -1397 |  | 320.3514
| 18 | 16 | Rule 250D BI- | 57 | 1 | PT:P1 | 270 | -316 | 1 | 130 | -155 | 1298 | 140 | -161 | -1298 |  | 341.6972
| 18 | 16 | Rule 250D BI- | 58 | 1 | PT:P2 | 270 | -316 | 1 | 130 | -155 | 1298 | 140 | -161 | -1298 |  | 341.6972
| 18 | 16 | Rule 250D BI- | 59 | 1 | PT:P3 | 270 | -316 | 1 | 130 | -155 | 1298 | 140 | -161 | -1298 |  | 341.6972
| 18 | 16 | Rule 250D BI- | 60 | 1 | PT:P4 | 270 | -316 | 1 | 130 | -155 | 1298 | 140 | -161 | -1298 |  | 341.6972
| 19 | 13 | NESC Insul NA+ | 1 | 1 | TL-S1 | 259 | -665 | -2 | 141 | -340 | 3733 | 118 | -326 | -3734
| 19 | 13 | NESC Insul NA+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 19 | 13 | NESC Insul NA+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 19 | 13 | NESC Insul NA+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 19 | 13 | NESC Insul NA+ | 10 | 1 | ST1 | 721 | -1611 | -2 | 377 | -816 | 11532 | 345 | -795 | -11534
| 19 | 13 | NESC Insul NA+ | 10 | 2 | ST2 | 721 | -1607 | -2 | 377 | -814 | 11532 | 345 | -793 | -11534
| 19 | 13 | NESC Insul NA+ | 10 | 3 | ST3 | 721 | -1603 | -2 | 377 | -812 | 11533 | 345 | -791 | -11535
| 19 | 13 | NESC Insul NA+ | 46 | 1 | F2 | 57 | 13 | -1 | 28 | 4 | 500 | 28 | 10 | -501
| 19 | 13 | NESC Insul NA+ | 49 | 1 | S1 | 150 | -552 | -1 | 81 | -281 | 3822 | 69 | -271 | -3823
| 19 | 13 | NESC Insul NA+ | 49 | 2 | S2 | 150 | -552 | -1 | 81 | -281 | 3822 | 69 | -271 | -3823
| 19 | 13 | NESC Insul NA+ | 49 | 3 | S3 | 150 | -553 | -1 | 81 | -282 | 3822 | 69 | -271 | -3823
| 19 | 13 | NESC Insul NA+ | 50 | 1 | S4 | 150 | -518 | -1 | 81 | -263 | 3824 | 69 | -255 | -3824
| 19 | 13 | NESC Insul NA+ | 50 | 2 | S5 | 150 | -517 | -1 | 81 | -263 | 3824 | 69 | -255 | -3824
| 19 | 13 | NESC Insul NA+ | 50 | 3 | S6 | 150 | -517 | -1 | 81 | -262 | 3824 | 69 | -254 | -3824
| 19 | 13 | NESC Insul NA+ | 53 | 1 | S7 | 70 | -73 | -1 | 35 | -39 | 892 | 34 | -33 | -893
| 19 | 13 | NESC Insul NA+ | 54 | 1 | S8 | 69 | -64 | -1 | 35 | -35 | 892 | 34 | -29 | -893
| 19 | 13 | NESC Insul NA+ | 57 | 1 | PT:P1 | 53 | 6 | -1 | 28 | -3 | 981 | 26 | 9 | -982
| 19 | 13 | NESC Insul NA+ | 58 | 1 | PT:P2 | 53 | 6 | -1 | 28 | -3 | 981 | 26 | 9 | -982
| 19 | 13 | NESC Insul NA+ | 59 | 1 | PT:P3 | 53 | 6 | -1 | 28 | -3 | 981 | 26 | 9 | -982
| 19 | 13 | NESC Insul NA+ | 60 | 1 | PT:P4 | 53 | 6 | -1 | 28 | -3 | 981 | 26 | 9 | -982
| 20 | 13 | NESC Insul NA- | 1 | 1 | TL-S1 | 259 | -875 | -1 | 141 | -438 | 3723 | 118 | -437 | -3723
| 20 | 13 | NESC Insul NA- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 20 | 13 | NESC Insul NA- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 20 | 13 | NESC Insul NA- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 20 | 13 | NESC Insul NA- | 10 | 1 | ST1 | 721 | -2400 | 2 | 377 | -1187 | 11504 | 345 | -1212 | -11502
| 20 | 13 | NESC Insul NA- | 10 | 2 | ST2 | 721 | -2395 | 2 | 377 | -1185 | 11504 | 345 | -1210 | -11502
| 20 | 13 | NESC Insul NA- | 10 | 3 | ST3 | 721 | -2391 | 2 | 377 | -1183 | 11504 | 345 | -1208 | -11502
| 20 | 13 | NESC Insul NA- | 46 | 1 | F2 | 57 | -185 | 1 | 28 | -89 | 492 | 28 | -96 | -491
| 20 | 13 | NESC Insul NA- | 49 | 1 | S1 | 150 | -834 | 1 | 81 | -413 | 3810 | 69 | -421 | -3810
| 20 | 13 | NESC Insul NA- | 49 | 2 | S2 | 150 | -834 | 1 | 81 | -413 | 3810 | 69 | -421 | -3810
| 20 | 13 | NESC Insul NA- | 49 | 3 | S3 | 150 | -835 | 1 | 81 | -413 | 3810 | 69 | -422 | -3810
| 20 | 13 | NESC Insul NA- | 50 | 1 | S4 | 150 | -799 | 1 | 81 | -394 | 3812 | 69 | -405 | -3811
| 20 | 13 | NESC Insul NA- | 50 | 2 | S5 | 150 | -799 | 1 | 81 | -394 | 3812 | 69 | -405 | -3811
| 20 | 13 | NESC Insul NA- | 50 | 3 | S6 | 150 | -798 | 1 | 81 | -394 | 3812 | 69 | -404 | -3812
| 20 | 13 | NESC Insul NA- | 53 | 1 | S7 | 70 | -251 | 0 | 35 | -123 | 885 | 34 | -128 | -884
| 20 | 13 | NESC Insul NA- | 54 | 1 | S8 | 69 | -242 | 1 | 35 | -118 | 885 | 34 | -124 | -885
| 20 | 13 | NESC Insul NA- | 57 | 1 | PT:P1 | 53 | -351 | 1 | 28 | -169 | 966 | 26 | -181 | -965
| 20 | 13 | NESC Insul NA- | 58 | 1 | PT:P2 | 53 | -351 | 1 | 28 | -169 | 966 | 26 | -181 | -965
| 20 | 13 | NESC Insul NA- | 59 | 1 | PT:P3 | 53 | -351 | 1 | 28 | -169 | 966 | 26 | -181 | -965
| 20 | 13 | NESC Insul NA- | 60 | 1 | PT:P4 | 53 | -351 | 1 | 28 | -169 | 966 | 26 | -181 | -965
| 21 | 12 | RULE 250C Insul NA+ | 1 | 1 | TL-S1 | 272 | -441 | -3 | 149 | -233 | 3742 | 123 | -207 | -3745
| 21 | 12 | RULE 250C Insul NA+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 21 | 12 | RULE 250C Insul NA+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 21 | 12 | RULE 250C Insul NA+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 21 | 12 | RULE 250C Insul NA+ | 10 | 1 | ST1 | 732 | -828 | -6 | 384 | -446 | 11979 | 348 | -383 | -11985
| 21 | 12 | RULE 250C Insul NA+ | 10 | 2 | ST2 | 732 | -842 | -6 | 384 | -452 | 11979 | 347 | -390 | -11985
| 21 | 12 | RULE 250C Insul NA+ | 10 | 3 | ST3 | 732 | -857 | -6 | 384 | -458 | 11978 | 347 | -398 | -11984
| 21 | 12 | RULE 250C Insul NA+ | 46 | 1 | F2 | 60 | 111 | -2 | 32 | 47 | 1041 | 28 | 64 | -1043
| 21 | 12 | RULE 250C Insul NA+ | 49 | 1 | S1 | 151 | -300 | -2 | 82 | -163 | 3885 | 69 | -137 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 49 | 2 | S2 | 151 | -304 | -2 | 82 | -165 | 3884 | 69 | -139 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 49 | 3 | S3 | 151 | -308 | -2 | 82 | -167 | 3884 | 69 | -141 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 50 | 1 | S4 | 151 | -267 | -2 | 82 | -145 | 3885 | 69 | -122 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 50 | 2 | S5 | 151 | -270 | -2 | 82 | -146 | 3885 | 69 | -123 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 50 | 3 | S6 | 151 | -273 | -2 | 82 | -148 | 3885 | 69 | -125 | -3887
| 21 | 12 | RULE 250C Insul NA+ | 53 | 1 | S7 | 73 | -5 | -1 | 39 | -10 | 1372 | 34 | 5 | -1373
| 21 | 12 | RULE 250C Insul NA+ | 54 | 1 | S8 | 73 | 9 | -1 | 39 | -3 | 1372 | 34 | 12 | -1373
| 21 | 12 | RULE 250C Insul NA+ | 57 | 1 | PT:P1 | 60 | 145 | -3 | 34 | 58 | 1916 | 26 | 87 | -1919
| 21 | 12 | RULE 250C Insul NA+ | 58 | 1 | PT:P2 | 60 | 144 | -3 | 34 | 58 | 1914 | 26 | 87 | -1917
| 21 | 12 | RULE 250C Insul NA+ | 59 | 1 | PT:P3 | 60 | 144 | -3 | 34 | 58 | 1912 | 26 | 87 | -1914
| 21 | 12 | RULE 250C Insul NA+ | 60 | 1 | PT:P4 | 60 | 144 | -3 | 34 | 57 | 1909 | 26 | 86 | -1912
| 22 | 12 | RULE 250C Insul NA- | 1 | 1 | TL-S1 | 272 | -1099 | 0 | 149 | -544 | 3711 | 123 | -556 | -3710
| 22 | 12 | RULE 250C Insul NA- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 22 | 12 | RULE 250C Insul NA- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 22 | 12 | RULE 250C Insul NA- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 22 | 12 | RULE 250C Insul NA- | 10 | 1 | ST1 | 732 | -3327 | 6 | 384 | -1630 | 11891 | 348 | -1697 | -11886
| 22 | 12 | RULE 250C Insul NA- | 10 | 2 | ST2 | 732 | -3306 | 5 | 384 | -1620 | 11892 | 347 | -1686 | -11887
| 22 | 12 | RULE 250C Insul NA- | 10 | 3 | ST3 | 732 | -3282 | 5 | 384 | -1608 | 11894 | 347 | -1674 | -11888
| 22 | 12 | RULE 250C Insul NA- | 46 | 1 | F2 | 60 | -466 | 2 | 32 | -224 | 1018 | 28 | -242 | -1016
| 22 | 12 | RULE 250C Insul NA- | 49 | 1 | S1 | 151 | -1104 | 2 | 82 | -540 | 3850 | 69 | -564 | -3848
| 22 | 12 | RULE 250C Insul NA- | 49 | 2 | S2 | 151 | -1101 | 2 | 82 | -539 | 3850 | 69 | -562 | -3848
| 22 | 12 | RULE 250C Insul NA- | 49 | 3 | S3 | 151 | -1098 | 2 | 82 | -538 | 3850 | 69 | -560 | -3849
| 22 | 12 | RULE 250C Insul NA- | 50 | 1 | S4 | 151 | -1068 | 2 | 82 | -521 | 3853 | 69 | -547 | -3851
| 22 | 12 | RULE 250C Insul NA- | 50 | 2 | S5 | 151 | -1064 | 2 | 82 | -519 | 3853 | 69 | -545 | -3851
| 22 | 12 | RULE 250C Insul NA- | 50 | 3 | S6 | 151 | -1060 | 2 | 82 | -518 | 3853 | 69 | -542 | -3851
| 22 | 12 | RULE 250C Insul NA- | 53 | 1 | S7 | 73 | -491 | 1 | 39 | -238 | 1351 | 34 | -253 | -1350
| 22 | 12 | RULE 250C Insul NA- | 54 | 1 | S8 | 73 | -477 | 1 | 39 | -231 | 1352 | 34 | -246 | -1351
| 22 | 12 | RULE 250C Insul NA- | 57 | 1 | PT:P1 | 60 | -816 | 3 | 34 | -393 | 1876 | 26 | -423 | -1874
| 22 | 12 | RULE 250C Insul NA- | 58 | 1 | PT:P2 | 60 | -815 | 3 | 34 | -393 | 1874 | 26 | -422 | -1872
| 22 | 12 | RULE 250C Insul NA- | 59 | 1 | PT:P3 | 60 | -814 | 3 | 34 | -392 | 1872 | 26 | -421 | -1869
| 22 | 12 | RULE 250C Insul NA- | 60 | 1 | PT:P4 | 60 | -813 | 3 | 34 | -392 | 1870 | 26 | -421 | -1867
| 23 | 16 | RULE 250D Insul NA+ | 1 | 1 | TL-S1 | 449 | -814 | -1 | 235 | -413 | 4267 | 214 | -400 | -4268 |  | 847.2438
| 23 | 16 | RULE 250D Insul NA+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 23 | 16 | RULE 250D Insul NA+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 23 | 16 | RULE 250D Insul NA+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 23 | 16 | RULE 250D Insul NA+ | 10 | 1 | ST1 | 1175 | -2177 | -1 | 597 | -1093 | 13556 | 578 | -1084 | -13557
| 23 | 16 | RULE 250D Insul NA+ | 10 | 2 | ST2 | 1175 | -2172 | -1 | 597 | -1090 | 13557 | 578 | -1082 | -13557
| 23 | 16 | RULE 250D Insul NA+ | 10 | 3 | ST3 | 1175 | -2167 | -1 | 597 | -1088 | 13557 | 578 | -1080 | -13558
| 23 | 16 | RULE 250D Insul NA+ | 46 | 1 | F2 | 207 | -65 | 0 | 100 | -35 | 763 | 107 | -31 | -763
| 23 | 16 | RULE 250D Insul NA+ | 49 | 1 | S1 | 338 | -748 | -1 | 171 | -377 | 4544 | 166 | -371 | -4545
| 23 | 16 | RULE 250D Insul NA+ | 49 | 2 | S2 | 338 | -748 | -1 | 171 | -377 | 4544 | 166 | -371 | -4545
| 23 | 16 | RULE 250D Insul NA+ | 49 | 3 | S3 | 338 | -749 | -1 | 171 | -378 | 4544 | 166 | -371 | -4545
| 23 | 16 | RULE 250D Insul NA+ | 50 | 1 | S4 | 336 | -707 | 0 | 171 | -355 | 4546 | 166 | -352 | -4546
| 23 | 16 | RULE 250D Insul NA+ | 50 | 2 | S5 | 336 | -706 | 0 | 171 | -355 | 4546 | 166 | -351 | -4546
| 23 | 16 | RULE 250D Insul NA+ | 50 | 3 | S6 | 336 | -706 | 0 | 171 | -355 | 4546 | 166 | -351 | -4546
| 23 | 16 | RULE 250D Insul NA+ | 53 | 1 | S7 | 214 | -192 | 0 | 105 | -98 | 1403 | 109 | -93 | -1403
| 23 | 16 | RULE 250D Insul NA+ | 54 | 1 | S8 | 213 | -178 | 0 | 104 | -91 | 1404 | 109 | -87 | -1404
| 23 | 16 | RULE 250D Insul NA+ | 57 | 1 | PT:P1 | 270 | -144 | -1 | 130 | -75 | 1306 | 140 | -69 | -1307
| 23 | 16 | RULE 250D Insul NA+ | 58 | 1 | PT:P2 | 270 | -144 | -1 | 130 | -75 | 1306 | 140 | -69 | -1307
| 23 | 16 | RULE 250D Insul NA+ | 59 | 1 | PT:P3 | 270 | -144 | -1 | 130 | -75 | 1306 | 140 | -69 | -1307
| 23 | 16 | RULE 250D Insul NA+ | 60 | 1 | PT:P4 | 270 | -144 | -1 | 130 | -75 | 1306 | 140 | -69 | -1307
| 24 | 16 | RULE 250D Insul NA- | 1 | 1 | TL-S1 | 449 | -948 | -1 | 235 | -476 | 4261 | 214 | -472 | -4261 |  | 976.6934
| 24 | 16 | RULE 250D Insul NA- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 24 | 16 | RULE 250D Insul NA- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 24 | 16 | RULE 250D Insul NA- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 24 | 16 | RULE 250D Insul NA- | 10 | 1 | ST1 | 1175 | -2541 | 1 | 597 | -1264 | 13543 | 578 | -1277 | -13541
| 24 | 16 | RULE 250D Insul NA- | 10 | 2 | ST2 | 1175 | -2536 | 1 | 597 | -1261 | 13543 | 578 | -1275 | -13542
| 24 | 16 | RULE 250D Insul NA- | 10 | 3 | ST3 | 1175 | -2531 | 1 | 597 | -1258 | 13543 | 578 | -1272 | -13542
| 24 | 16 | RULE 250D Insul NA- | 46 | 1 | F2 | 207 | -197 | 0 | 100 | -96 | 757 | 107 | -101 | -757
| 24 | 16 | RULE 250D Insul NA- | 49 | 1 | S1 | 338 | -901 | 0 | 171 | -449 | 4538 | 166 | -452 | -4537
| 24 | 16 | RULE 250D Insul NA- | 49 | 2 | S2 | 338 | -902 | 0 | 171 | -449 | 4538 | 166 | -453 | -4537
| 24 | 16 | RULE 250D Insul NA- | 49 | 3 | S3 | 338 | -902 | 0 | 171 | -449 | 4537 | 166 | -453 | -4537
| 24 | 16 | RULE 250D Insul NA- | 50 | 1 | S4 | 336 | -860 | 1 | 171 | -427 | 4540 | 166 | -433 | -4539
| 24 | 16 | RULE 250D Insul NA- | 50 | 2 | S5 | 336 | -859 | 1 | 171 | -426 | 4540 | 166 | -433 | -4539
| 24 | 16 | RULE 250D Insul NA- | 50 | 3 | S6 | 336 | -859 | 1 | 171 | -426 | 4540 | 166 | -433 | -4539
| 24 | 16 | RULE 250D Insul NA- | 53 | 1 | S7 | 214 | -318 | 0 | 105 | -157 | 1398 | 109 | -161 | -1397
| 24 | 16 | RULE 250D Insul NA- | 54 | 1 | S8 | 213 | -304 | 0 | 104 | -150 | 1398 | 109 | -154 | -1398
| 24 | 16 | RULE 250D Insul NA- | 57 | 1 | PT:P1 | 270 | -317 | 1 | 130 | -156 | 1299 | 140 | -161 | -1299
| 24 | 16 | RULE 250D Insul NA- | 58 | 1 | PT:P2 | 270 | -317 | 1 | 130 | -156 | 1299 | 140 | -161 | -1299
| 24 | 16 | RULE 250D Insul NA- | 59 | 1 | PT:P3 | 270 | -317 | 1 | 130 | -156 | 1299 | 140 | -161 | -1299
| 24 | 16 | RULE 250D Insul NA- | 60 | 1 | PT:P4 | 270 | -317 | 1 | 130 | -156 | 1299 | 140 | -161 | -1299
| 25 | 29 | MIN TEMP | 1 | 1 | TL-S1 | 299 | -884 | -1 | 165 | -446 | 4280 | 134 | -438 | -4281
| 25 | 29 | MIN TEMP | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 25 | 29 | MIN TEMP | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 25 | 29 | MIN TEMP | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 25 | 29 | MIN TEMP | 10 | 1 | ST1 | 747 | -2288 | 0 | 396 | -1143 | 13141 | 352 | -1145 | -13141
| 25 | 29 | MIN TEMP | 10 | 2 | ST2 | 747 | -2283 | 0 | 396 | -1140 | 13141 | 352 | -1143 | -13141
| 25 | 29 | MIN TEMP | 10 | 3 | ST3 | 747 | -2278 | 0 | 396 | -1138 | 13141 | 352 | -1141 | -13141
| 25 | 29 | MIN TEMP | 46 | 1 | F2 | 55 | -29 | 0 | 27 | -15 | 168 | 28 | -15 | -168
| 25 | 29 | MIN TEMP | 49 | 1 | S1 | 154 | -826 | 0 | 86 | -414 | 4551 | 68 | -413 | -4551
| 25 | 29 | MIN TEMP | 49 | 2 | S2 | 154 | -827 | 0 | 86 | -414 | 4551 | 68 | -413 | -4551
| 25 | 29 | MIN TEMP | 49 | 3 | S3 | 154 | -827 | 0 | 86 | -414 | 4551 | 68 | -413 | -4551
| 25 | 29 | MIN TEMP | 50 | 1 | S4 | 154 | -785 | 0 | 86 | -392 | 4553 | 68 | -393 | -4553
| 25 | 29 | MIN TEMP | 50 | 2 | S5 | 154 | -785 | 0 | 86 | -392 | 4553 | 68 | -393 | -4553
| 25 | 29 | MIN TEMP | 50 | 3 | S6 | 154 | -784 | 0 | 86 | -391 | 4553 | 68 | -393 | -4553
| 25 | 29 | MIN TEMP | 53 | 1 | S7 | 69 | -129 | 0 | 35 | -65 | 709 | 34 | -64 | -709
| 25 | 29 | MIN TEMP | 54 | 1 | S8 | 69 | -122 | 0 | 35 | -61 | 709 | 34 | -61 | -709
| 25 | 29 | MIN TEMP | 57 | 1 | PT:P1 | 49 | -56 | 0 | 24 | -28 | 314 | 25 | -28 | -314
| 25 | 29 | MIN TEMP | 58 | 1 | PT:P2 | 49 | -56 | 0 | 24 | -28 | 314 | 25 | -28 | -314
| 25 | 29 | MIN TEMP | 59 | 1 | PT:P3 | 49 | -56 | 0 | 24 | -28 | 314 | 25 | -28 | -314
| 25 | 29 | MIN TEMP | 60 | 1 | PT:P4 | 49 | -56 | 0 | 24 | -28 | 314 | 25 | -28 | -314
| 26 | 27 | Crack Check+ | 1 | 1 | TL-S1 | 262 | -676 | -1 | 142 | -344 | 3647 | 120 | -332 | -3649
| 26 | 27 | Crack Check+ | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 26 | 27 | Crack Check+ | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 26 | 27 | Crack Check+ | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 26 | 27 | Crack Check+ | 10 | 1 | ST1 | 763 | -1623 | -1 | 392 | -819 | 10993 | 371 | -804 | -10995
| 26 | 27 | Crack Check+ | 10 | 2 | ST2 | 763 | -1619 | -1 | 392 | -817 | 10993 | 371 | -802 | -10995
| 26 | 27 | Crack Check+ | 10 | 3 | ST3 | 763 | -1615 | -1 | 392 | -815 | 10993 | 371 | -800 | -10995
| 26 | 27 | Crack Check+ | 46 | 1 | F2 | 59 | 3 | 0 | 30 | -1 | 407 | 30 | 4 | -407
| 26 | 27 | Crack Check+ | 49 | 1 | S1 | 160 | -507 | -1 | 84 | -258 | 3369 | 76 | -250 | -3370
| 26 | 27 | Crack Check+ | 49 | 2 | S2 | 160 | -508 | -1 | 84 | -258 | 3369 | 76 | -250 | -3370
| 26 | 27 | Crack Check+ | 49 | 3 | S3 | 160 | -508 | -1 | 84 | -258 | 3369 | 76 | -250 | -3370
| 26 | 27 | Crack Check+ | 50 | 1 | S4 | 159 | -477 | -1 | 84 | -242 | 3370 | 75 | -236 | -3371
| 26 | 27 | Crack Check+ | 50 | 2 | S5 | 159 | -477 | -1 | 84 | -241 | 3370 | 75 | -236 | -3371
| 26 | 27 | Crack Check+ | 50 | 3 | S6 | 159 | -477 | -1 | 84 | -241 | 3371 | 75 | -235 | -3371
| 26 | 27 | Crack Check+ | 53 | 1 | S7 | 73 | -58 | 0 | 37 | -31 | 682 | 37 | -27 | -682
| 26 | 27 | Crack Check+ | 54 | 1 | S8 | 73 | -51 | 0 | 37 | -28 | 682 | 37 | -24 | -682
| 26 | 27 | Crack Check+ | 57 | 1 | PT:P1 | 57 | -9 | -1 | 29 | -9 | 794 | 28 | 0 | -795
| 26 | 27 | Crack Check+ | 58 | 1 | PT:P2 | 57 | -9 | -1 | 29 | -9 | 794 | 28 | 0 | -795
| 26 | 27 | Crack Check+ | 59 | 1 | PT:P3 | 57 | -9 | -1 | 29 | -9 | 794 | 28 | 0 | -795
| 26 | 27 | Crack Check+ | 60 | 1 | PT:P4 | 57 | -9 | -1 | 29 | -9 | 794 | 28 | 0 | -795
| 27 | 27 | Crack Check- | 1 | 1 | TL-S1 | 262 | -830 | -1 | 142 | -416 | 3640 | 120 | -414 | -3641
| 27 | 27 | Crack Check- | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 27 | 27 | Crack Check- | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 27 | 27 | Crack Check- | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 27 | 27 | Crack Check- | 10 | 1 | ST1 | 763 | -2201 | 2 | 392 | -1091 | 10972 | 371 | -1110 | -10971
| 27 | 27 | Crack Check- | 10 | 2 | ST2 | 763 | -2197 | 2 | 392 | -1089 | 10973 | 371 | -1108 | -10971
| 27 | 27 | Crack Check- | 10 | 3 | ST3 | 763 | -2193 | 2 | 392 | -1087 | 10973 | 371 | -1106 | -10971
| 27 | 27 | Crack Check- | 46 | 1 | F2 | 59 | -143 | 0 | 30 | -69 | 401 | 30 | -74 | -401
| 27 | 27 | Crack Check- | 49 | 1 | S1 | 160 | -714 | 1 | 84 | -354 | 3361 | 76 | -360 | -3360
| 27 | 27 | Crack Check- | 49 | 2 | S2 | 160 | -715 | 1 | 84 | -354 | 3360 | 76 | -360 | -3360
| 27 | 27 | Crack Check- | 49 | 3 | S3 | 160 | -715 | 1 | 84 | -355 | 3360 | 76 | -361 | -3360
| 27 | 27 | Crack Check- | 50 | 1 | S4 | 159 | -684 | 1 | 84 | -338 | 3362 | 75 | -346 | -3362
| 27 | 27 | Crack Check- | 50 | 2 | S5 | 159 | -683 | 1 | 84 | -338 | 3362 | 75 | -346 | -3362
| 27 | 27 | Crack Check- | 50 | 3 | S6 | 159 | -683 | 1 | 84 | -338 | 3362 | 75 | -345 | -3362
| 27 | 27 | Crack Check- | 53 | 1 | S7 | 73 | -189 | 0 | 37 | -92 | 676 | 37 | -97 | -676
| 27 | 27 | Crack Check- | 54 | 1 | S8 | 73 | -182 | 0 | 37 | -89 | 677 | 37 | -93 | -676
| 27 | 27 | Crack Check- | 57 | 1 | PT:P1 | 57 | -270 | 1 | 29 | -131 | 783 | 28 | -139 | -782
| 27 | 27 | Crack Check- | 58 | 1 | PT:P2 | 57 | -270 | 1 | 29 | -131 | 783 | 28 | -139 | -782
| 27 | 27 | Crack Check- | 59 | 1 | PT:P3 | 57 | -270 | 1 | 29 | -131 | 783 | 28 | -139 | -782
| 27 | 27 | Crack Check- | 60 | 1 | PT:P4 | 57 | -270 | 1 | 29 | -131 | 783 | 28 | -139 | -782
| 28 | 12 | Hurr -90 | 1 | 1 | TL-S1 | 259 | -740 | -1 | 140 | -375 | 3583 | 119 | -365 | -3585
| 28 | 12 | Hurr -90 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 28 | 12 | Hurr -90 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 28 | 12 | Hurr -90 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 28 | 12 | Hurr -90 | 10 | 1 | ST1 | 759 | -1864 | -1 | 390 | -935 | 10707 | 370 | -928 | -10708
| 28 | 12 | Hurr -90 | 10 | 2 | ST2 | 759 | -1860 | -1 | 390 | -933 | 10708 | 370 | -927 | -10708
| 28 | 12 | Hurr -90 | 10 | 3 | ST3 | 759 | -1856 | -1 | 390 | -931 | 10708 | 370 | -925 | -10708
| 28 | 12 | Hurr -90 | 46 | 1 | F2 | 58 | -34 | 0 | 28 | -18 | 198 | 30 | -16 | -198
| 28 | 12 | Hurr -90 | 49 | 1 | S1 | 159 | -583 | 0 | 83 | -294 | 3213 | 76 | -289 | -3213
| 28 | 12 | Hurr -90 | 49 | 2 | S2 | 159 | -583 | 0 | 83 | -294 | 3213 | 76 | -289 | -3213
| 28 | 12 | Hurr -90 | 49 | 3 | S3 | 159 | -584 | 0 | 83 | -294 | 3213 | 76 | -290 | -3213
| 28 | 12 | Hurr -90 | 50 | 1 | S4 | 159 | -554 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 28 | 12 | Hurr -90 | 50 | 2 | S5 | 159 | -554 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 28 | 12 | Hurr -90 | 50 | 3 | S6 | 159 | -553 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 28 | 12 | Hurr -90 | 53 | 1 | S7 | 72 | -86 | 0 | 35 | -44 | 474 | 37 | -42 | -474
| 28 | 12 | Hurr -90 | 54 | 1 | S8 | 72 | -81 | 0 | 35 | -42 | 474 | 36 | -40 | -474
| 28 | 12 | Hurr -90 | 57 | 1 | PT:P1 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 28 | 12 | Hurr -90 | 58 | 1 | PT:P2 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 28 | 12 | Hurr -90 | 59 | 1 | PT:P3 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 28 | 12 | Hurr -90 | 60 | 1 | PT:P4 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 29 | 12 | Hurr -85 | 1 | 1 | TL-S1 | 259 | -733 | -1 | 140 | -373 | 3584 | 119 | -360 | -3585
| 29 | 12 | Hurr -85 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 29 | 12 | Hurr -85 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 29 | 12 | Hurr -85 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 29 | 12 | Hurr -85 | 10 | 1 | ST1 | 759 | -1829 | -1 | 390 | -923 | 10708 | 370 | -906 | -10709
| 29 | 12 | Hurr -85 | 10 | 2 | ST2 | 759 | -1825 | -1 | 390 | -921 | 10708 | 370 | -904 | -10709
| 29 | 12 | Hurr -85 | 10 | 3 | ST3 | 759 | -1822 | -1 | 390 | -919 | 10708 | 370 | -903 | -10710
| 29 | 12 | Hurr -85 | 46 | 1 | F2 | 58 | -29 | 0 | 28 | -17 | 198 | 30 | -12 | -198
| 29 | 12 | Hurr -85 | 49 | 1 | S1 | 159 | -576 | -1 | 83 | -292 | 3213 | 76 | -284 | -3214
| 29 | 12 | Hurr -85 | 49 | 2 | S2 | 159 | -576 | -1 | 83 | -292 | 3213 | 76 | -284 | -3214
| 29 | 12 | Hurr -85 | 49 | 3 | S3 | 159 | -577 | -1 | 83 | -292 | 3213 | 76 | -284 | -3214
| 29 | 12 | Hurr -85 | 50 | 1 | S4 | 159 | -547 | -1 | 83 | -277 | 3214 | 75 | -271 | -3215
| 29 | 12 | Hurr -85 | 50 | 2 | S5 | 159 | -547 | -1 | 83 | -276 | 3214 | 75 | -271 | -3215
| 29 | 12 | Hurr -85 | 50 | 3 | S6 | 159 | -547 | -1 | 83 | -276 | 3214 | 75 | -270 | -3215
| 29 | 12 | Hurr -85 | 53 | 1 | S7 | 72 | -82 | 0 | 35 | -43 | 474 | 37 | -39 | -474
| 29 | 12 | Hurr -85 | 54 | 1 | S8 | 72 | -77 | 0 | 35 | -41 | 474 | 36 | -37 | -474
| 29 | 12 | Hurr -85 | 57 | 1 | PT:P1 | 54 | -50 | -1 | 26 | -29 | 329 | 28 | -21 | -329
| 29 | 12 | Hurr -85 | 58 | 1 | PT:P2 | 54 | -50 | -1 | 26 | -29 | 329 | 28 | -21 | -329
| 29 | 12 | Hurr -85 | 59 | 1 | PT:P3 | 54 | -50 | -1 | 26 | -29 | 329 | 28 | -21 | -329
| 29 | 12 | Hurr -85 | 60 | 1 | PT:P4 | 54 | -50 | -1 | 26 | -29 | 329 | 28 | -21 | -329
| 30 | 12 | Hurr -80 | 1 | 1 | TL-S1 | 259 | -724 | -2 | 140 | -372 | 3584 | 119 | -352 | -3586
| 30 | 12 | Hurr -80 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 30 | 12 | Hurr -80 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 30 | 12 | Hurr -80 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 30 | 12 | Hurr -80 | 10 | 1 | ST1 | 759 | -1785 | -3 | 390 | -910 | 10708 | 370 | -874 | -10711
| 30 | 12 | Hurr -80 | 10 | 2 | ST2 | 759 | -1782 | -3 | 390 | -908 | 10708 | 370 | -873 | -10711
| 30 | 12 | Hurr -80 | 10 | 3 | ST3 | 759 | -1779 | -3 | 390 | -906 | 10708 | 370 | -872 | -10711
| 30 | 12 | Hurr -80 | 46 | 1 | F2 | 58 | -23 | -1 | 28 | -16 | 203 | 30 | -6 | -204
| 30 | 12 | Hurr -80 | 49 | 1 | S1 | 159 | -566 | -1 | 83 | -291 | 3213 | 76 | -275 | -3214
| 30 | 12 | Hurr -80 | 49 | 2 | S2 | 159 | -566 | -1 | 83 | -291 | 3213 | 76 | -275 | -3214
| 30 | 12 | Hurr -80 | 49 | 3 | S3 | 159 | -567 | -1 | 83 | -291 | 3213 | 76 | -276 | -3214
| 30 | 12 | Hurr -80 | 50 | 1 | S4 | 159 | -537 | -1 | 83 | -275 | 3214 | 75 | -262 | -3215
| 30 | 12 | Hurr -80 | 50 | 2 | S5 | 159 | -537 | -1 | 83 | -275 | 3214 | 75 | -262 | -3215
| 30 | 12 | Hurr -80 | 50 | 3 | S6 | 159 | -537 | -1 | 83 | -275 | 3214 | 75 | -262 | -3215
| 30 | 12 | Hurr -80 | 53 | 1 | S7 | 72 | -76 | -1 | 35 | -43 | 478 | 37 | -34 | -478
| 30 | 12 | Hurr -80 | 54 | 1 | S8 | 72 | -72 | -1 | 35 | -40 | 478 | 36 | -32 | -479
| 30 | 12 | Hurr -80 | 57 | 1 | PT:P1 | 54 | -40 | -2 | 26 | -28 | 341 | 28 | -11 | -343
| 30 | 12 | Hurr -80 | 58 | 1 | PT:P2 | 54 | -40 | -2 | 26 | -28 | 341 | 28 | -11 | -343
| 30 | 12 | Hurr -80 | 59 | 1 | PT:P3 | 54 | -40 | -2 | 26 | -28 | 341 | 28 | -11 | -343
| 30 | 12 | Hurr -80 | 60 | 1 | PT:P4 | 54 | -40 | -2 | 26 | -28 | 341 | 28 | -11 | -342
| 31 | 12 | Hurr -75 | 1 | 1 | TL-S1 | 259 | -711 | -3 | 141 | -368 | 3588 | 119 | -342 | -3591
| 31 | 12 | Hurr -75 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 31 | 12 | Hurr -75 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 31 | 12 | Hurr -75 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 31 | 12 | Hurr -75 | 10 | 1 | ST1 | 760 | -1728 | -5 | 390 | -892 | 10730 | 370 | -837 | -10735
| 31 | 12 | Hurr -75 | 10 | 2 | ST2 | 760 | -1726 | -5 | 390 | -890 | 10731 | 370 | -836 | -10735
| 31 | 12 | Hurr -75 | 10 | 3 | ST3 | 760 | -1724 | -5 | 390 | -888 | 10731 | 370 | -836 | -10735
| 31 | 12 | Hurr -75 | 46 | 1 | F2 | 58 | -15 | -1 | 28 | -15 | 225 | 30 | 0 | -226
| 31 | 12 | Hurr -75 | 49 | 1 | S1 | 159 | -551 | -2 | 83 | -287 | 3224 | 76 | -264 | -3226
| 31 | 12 | Hurr -75 | 49 | 2 | S2 | 159 | -552 | -2 | 83 | -287 | 3224 | 76 | -265 | -3226
| 31 | 12 | Hurr -75 | 49 | 3 | S3 | 159 | -553 | -2 | 83 | -288 | 3224 | 76 | -265 | -3226
| 31 | 12 | Hurr -75 | 50 | 1 | S4 | 159 | -523 | -2 | 83 | -271 | 3226 | 75 | -251 | -3227
| 31 | 12 | Hurr -75 | 50 | 2 | S5 | 159 | -523 | -2 | 83 | -271 | 3226 | 75 | -251 | -3227
| 31 | 12 | Hurr -75 | 50 | 3 | S6 | 159 | -522 | -2 | 83 | -271 | 3226 | 75 | -252 | -3227
| 31 | 12 | Hurr -75 | 53 | 1 | S7 | 72 | -69 | -1 | 36 | -41 | 493 | 37 | -28 | -494
| 31 | 12 | Hurr -75 | 54 | 1 | S8 | 72 | -64 | -1 | 36 | -38 | 493 | 37 | -26 | -495
| 31 | 12 | Hurr -75 | 57 | 1 | PT:P1 | 54 | -28 | -2 | 26 | -27 | 388 | 28 | -1 | -390
| 31 | 12 | Hurr -75 | 58 | 1 | PT:P2 | 54 | -28 | -2 | 26 | -27 | 387 | 28 | -1 | -390
| 31 | 12 | Hurr -75 | 59 | 1 | PT:P3 | 54 | -28 | -2 | 26 | -27 | 387 | 28 | -1 | -390
| 31 | 12 | Hurr -75 | 60 | 1 | PT:P4 | 54 | -28 | -2 | 26 | -27 | 387 | 28 | -1 | -390
| 32 | 12 | Hurr -70 | 1 | 1 | TL-S1 | 260 | -695 | -3 | 141 | -364 | 3602 | 119 | -331 | -3605
| 32 | 12 | Hurr -70 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 32 | 12 | Hurr -70 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 32 | 12 | Hurr -70 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 32 | 12 | Hurr -70 | 10 | 1 | ST1 | 760 | -1661 | -6 | 390 | -867 | 10775 | 370 | -794 | -10781
| 32 | 12 | Hurr -70 | 10 | 2 | ST2 | 760 | -1659 | -6 | 390 | -865 | 10775 | 370 | -794 | -10781
| 32 | 12 | Hurr -70 | 10 | 3 | ST3 | 760 | -1658 | -6 | 390 | -864 | 10775 | 370 | -794 | -10781
| 32 | 12 | Hurr -70 | 46 | 1 | F2 | 59 | -7 | -2 | 29 | -13 | 271 | 30 | 7 | -273
| 32 | 12 | Hurr -70 | 49 | 1 | S1 | 159 | -534 | -3 | 83 | -282 | 3252 | 76 | -252 | -3255
| 32 | 12 | Hurr -70 | 49 | 2 | S2 | 159 | -535 | -3 | 83 | -282 | 3252 | 76 | -253 | -3255
| 32 | 12 | Hurr -70 | 49 | 3 | S3 | 159 | -536 | -3 | 83 | -283 | 3252 | 76 | -253 | -3255
| 32 | 12 | Hurr -70 | 50 | 1 | S4 | 159 | -505 | -2 | 83 | -266 | 3254 | 75 | -239 | -3256
| 32 | 12 | Hurr -70 | 50 | 2 | S5 | 159 | -505 | -2 | 83 | -266 | 3254 | 75 | -240 | -3256
| 32 | 12 | Hurr -70 | 50 | 3 | S6 | 159 | -506 | -2 | 83 | -266 | 3254 | 75 | -240 | -3256
| 32 | 12 | Hurr -70 | 53 | 1 | S7 | 72 | -63 | -2 | 36 | -40 | 530 | 37 | -22 | -532
| 32 | 12 | Hurr -70 | 54 | 1 | S8 | 72 | -57 | -1 | 36 | -37 | 531 | 37 | -20 | -532
| 32 | 12 | Hurr -70 | 57 | 1 | PT:P1 | 55 | -18 | -3 | 27 | -26 | 482 | 28 | 8 | -485
| 32 | 12 | Hurr -70 | 58 | 1 | PT:P2 | 55 | -18 | -3 | 27 | -26 | 482 | 28 | 8 | -485
| 32 | 12 | Hurr -70 | 59 | 1 | PT:P3 | 55 | -18 | -3 | 27 | -26 | 482 | 28 | 8 | -485
| 32 | 12 | Hurr -70 | 60 | 1 | PT:P4 | 55 | -19 | -3 | 27 | -26 | 482 | 28 | 8 | -484
| 33 | 12 | Hurr -65 | 1 | 1 | TL-S1 | 261 | -677 | -4 | 141 | -358 | 3624 | 120 | -319 | -3628
| 33 | 12 | Hurr -65 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 33 | 12 | Hurr -65 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 33 | 12 | Hurr -65 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 33 | 12 | Hurr -65 | 10 | 1 | ST1 | 762 | -1591 | -8 | 391 | -840 | 10883 | 370 | -751 | -10891
| 33 | 12 | Hurr -65 | 10 | 2 | ST2 | 761 | -1591 | -8 | 391 | -839 | 10883 | 370 | -752 | -10891
| 33 | 12 | Hurr -65 | 10 | 3 | ST3 | 761 | -1591 | -7 | 391 | -838 | 10883 | 370 | -753 | -10891
| 33 | 12 | Hurr -65 | 46 | 1 | F2 | 59 | 1 | -2 | 29 | -12 | 341 | 30 | 13 | -343
| 33 | 12 | Hurr -65 | 49 | 1 | S1 | 159 | -516 | -3 | 84 | -276 | 3302 | 76 | -240 | -3305
| 33 | 12 | Hurr -65 | 49 | 2 | S2 | 159 | -517 | -3 | 84 | -277 | 3302 | 76 | -241 | -3305
| 33 | 12 | Hurr -65 | 49 | 3 | S3 | 159 | -518 | -3 | 84 | -277 | 3302 | 76 | -241 | -3305
| 33 | 12 | Hurr -65 | 50 | 1 | S4 | 159 | -487 | -3 | 84 | -260 | 3303 | 75 | -227 | -3306
| 33 | 12 | Hurr -65 | 50 | 2 | S5 | 159 | -487 | -3 | 84 | -260 | 3303 | 75 | -227 | -3306
| 33 | 12 | Hurr -65 | 50 | 3 | S6 | 159 | -487 | -3 | 84 | -260 | 3303 | 75 | -228 | -3306
| 33 | 12 | Hurr -65 | 53 | 1 | S7 | 73 | -58 | -2 | 36 | -40 | 594 | 37 | -18 | -596
| 33 | 12 | Hurr -65 | 54 | 1 | S8 | 73 | -52 | -2 | 36 | -36 | 594 | 37 | -16 | -596
| 33 | 12 | Hurr -65 | 57 | 1 | PT:P1 | 56 | -10 | -4 | 28 | -26 | 619 | 28 | 16 | -623
| 33 | 12 | Hurr -65 | 58 | 1 | PT:P2 | 56 | -10 | -4 | 28 | -26 | 619 | 28 | 16 | -623
| 33 | 12 | Hurr -65 | 59 | 1 | PT:P3 | 56 | -10 | -4 | 28 | -26 | 618 | 28 | 16 | -622
| 33 | 12 | Hurr -65 | 60 | 1 | PT:P4 | 56 | -10 | -4 | 28 | -26 | 618 | 28 | 16 | -621
| 34 | 12 | Hurr -60 | 1 | 1 | TL-S1 | 263 | -660 | -4 | 143 | -352 | 3668 | 120 | -308 | -3673
| 34 | 12 | Hurr -60 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 34 | 12 | Hurr -60 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 34 | 12 | Hurr -60 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 34 | 12 | Hurr -60 | 10 | 1 | ST1 | 764 | -1524 | -9 | 393 | -814 | 11065 | 371 | -709 | -11074
| 34 | 12 | Hurr -60 | 10 | 2 | ST2 | 764 | -1525 | -9 | 393 | -814 | 11065 | 371 | -711 | -11074
| 34 | 12 | Hurr -60 | 10 | 3 | ST3 | 764 | -1526 | -9 | 393 | -813 | 11065 | 371 | -713 | -11074
| 34 | 12 | Hurr -60 | 46 | 1 | F2 | 59 | 8 | -2 | 30 | -10 | 428 | 30 | 18 | -430
| 34 | 12 | Hurr -60 | 49 | 1 | S1 | 160 | -499 | -4 | 84 | -270 | 3379 | 76 | -228 | -3383
| 34 | 12 | Hurr -60 | 49 | 2 | S2 | 160 | -500 | -4 | 84 | -271 | 3379 | 76 | -229 | -3383
| 34 | 12 | Hurr -60 | 49 | 3 | S3 | 160 | -501 | -4 | 84 | -271 | 3379 | 76 | -230 | -3383
| 34 | 12 | Hurr -60 | 50 | 1 | S4 | 159 | -469 | -3 | 84 | -254 | 3380 | 75 | -215 | -3384
| 34 | 12 | Hurr -60 | 50 | 2 | S5 | 159 | -469 | -3 | 84 | -254 | 3380 | 75 | -216 | -3384
| 34 | 12 | Hurr -60 | 50 | 3 | S6 | 159 | -470 | -3 | 84 | -254 | 3380 | 75 | -216 | -3384
| 34 | 12 | Hurr -60 | 53 | 1 | S7 | 73 | -54 | -2 | 37 | -40 | 681 | 37 | -15 | -683
| 34 | 12 | Hurr -60 | 54 | 1 | S8 | 73 | -48 | -2 | 37 | -36 | 681 | 37 | -12 | -683
| 34 | 12 | Hurr -60 | 57 | 1 | PT:P1 | 57 | -2 | -4 | 29 | -25 | 784 | 28 | 23 | -789
| 34 | 12 | Hurr -60 | 58 | 1 | PT:P2 | 57 | -2 | -4 | 29 | -25 | 783 | 28 | 23 | -788
| 34 | 12 | Hurr -60 | 59 | 1 | PT:P3 | 57 | -2 | -4 | 29 | -25 | 782 | 28 | 23 | -787
| 34 | 12 | Hurr -60 | 60 | 1 | PT:P4 | 57 | -2 | -4 | 29 | -25 | 782 | 28 | 23 | -786
| 35 | 12 | Hurr -55 | 1 | 1 | TL-S1 | 265 | -643 | -5 | 144 | -345 | 3721 | 121 | -297 | -3726
| 35 | 12 | Hurr -55 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 35 | 12 | Hurr -55 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 35 | 12 | Hurr -55 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 35 | 12 | Hurr -55 | 10 | 1 | ST1 | 767 | -1459 | -10 | 395 | -789 | 11309 | 372 | -671 | -11320
| 35 | 12 | Hurr -55 | 10 | 2 | ST2 | 767 | -1462 | -10 | 395 | -789 | 11309 | 372 | -673 | -11319
| 35 | 12 | Hurr -55 | 10 | 3 | ST3 | 767 | -1465 | -10 | 395 | -789 | 11309 | 372 | -676 | -11319
| 35 | 12 | Hurr -55 | 46 | 1 | F2 | 60 | 17 | -3 | 30 | -8 | 524 | 30 | 24 | -527
| 35 | 12 | Hurr -55 | 49 | 1 | S1 | 160 | -484 | -4 | 85 | -265 | 3488 | 76 | -218 | -3492
| 35 | 12 | Hurr -55 | 49 | 2 | S2 | 160 | -485 | -4 | 85 | -266 | 3488 | 76 | -219 | -3492
| 35 | 12 | Hurr -55 | 49 | 3 | S3 | 160 | -487 | -4 | 85 | -267 | 3488 | 76 | -220 | -3492
| 35 | 12 | Hurr -55 | 50 | 1 | S4 | 160 | -453 | -4 | 84 | -248 | 3489 | 75 | -205 | -3493
| 35 | 12 | Hurr -55 | 50 | 2 | S5 | 160 | -453 | -4 | 84 | -248 | 3489 | 75 | -205 | -3493
| 35 | 12 | Hurr -55 | 50 | 3 | S6 | 160 | -454 | -4 | 84 | -248 | 3489 | 75 | -206 | -3493
| 35 | 12 | Hurr -55 | 53 | 1 | S7 | 74 | -52 | -3 | 37 | -40 | 784 | 37 | -12 | -787
| 35 | 12 | Hurr -55 | 54 | 1 | S8 | 74 | -45 | -2 | 37 | -36 | 785 | 37 | -9 | -787
| 35 | 12 | Hurr -55 | 57 | 1 | PT:P1 | 58 | 8 | -5 | 30 | -23 | 964 | 28 | 31 | -969
| 35 | 12 | Hurr -55 | 58 | 1 | PT:P2 | 58 | 8 | -5 | 30 | -23 | 963 | 28 | 31 | -968
| 35 | 12 | Hurr -55 | 59 | 1 | PT:P3 | 58 | 8 | -5 | 30 | -23 | 962 | 28 | 31 | -967
| 35 | 12 | Hurr -55 | 60 | 1 | PT:P4 | 58 | 8 | -5 | 30 | -23 | 961 | 28 | 31 | -966
| 36 | 12 | Hurr -50 | 1 | 1 | TL-S1 | 269 | -628 | -5 | 146 | -340 | 3796 | 123 | -288 | -3801
| 36 | 12 | Hurr -50 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 36 | 12 | Hurr -50 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 36 | 12 | Hurr -50 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 36 | 12 | Hurr -50 | 10 | 1 | ST1 | 770 | -1402 | -11 | 398 | -765 | 11625 | 373 | -637 | -11636
| 36 | 12 | Hurr -50 | 10 | 2 | ST2 | 770 | -1406 | -11 | 398 | -766 | 11625 | 373 | -640 | -11636
| 36 | 12 | Hurr -50 | 10 | 3 | ST3 | 770 | -1410 | -11 | 398 | -767 | 11624 | 373 | -644 | -11635
| 36 | 12 | Hurr -50 | 46 | 1 | F2 | 61 | 26 | -3 | 31 | -4 | 624 | 30 | 30 | -627
| 36 | 12 | Hurr -50 | 49 | 1 | S1 | 161 | -470 | -5 | 85 | -261 | 3617 | 76 | -209 | -3622
| 36 | 12 | Hurr -50 | 49 | 2 | S2 | 161 | -472 | -5 | 85 | -261 | 3617 | 76 | -210 | -3622
| 36 | 12 | Hurr -50 | 49 | 3 | S3 | 161 | -474 | -5 | 85 | -262 | 3617 | 76 | -212 | -3621
| 36 | 12 | Hurr -50 | 50 | 1 | S4 | 160 | -438 | -4 | 85 | -243 | 3618 | 75 | -195 | -3622
| 36 | 12 | Hurr -50 | 50 | 2 | S5 | 160 | -439 | -4 | 85 | -243 | 3618 | 75 | -196 | -3622
| 36 | 12 | Hurr -50 | 50 | 3 | S6 | 160 | -440 | -4 | 85 | -243 | 3618 | 75 | -197 | -3622
| 36 | 12 | Hurr -50 | 53 | 1 | S7 | 75 | -50 | -3 | 38 | -41 | 897 | 37 | -10 | -900
| 36 | 12 | Hurr -50 | 54 | 1 | S8 | 74 | -42 | -3 | 38 | -35 | 898 | 37 | -6 | -901
| 36 | 12 | Hurr -50 | 57 | 1 | PT:P1 | 59 | 19 | -5 | 31 | -20 | 1150 | 28 | 39 | -1155
| 36 | 12 | Hurr -50 | 58 | 1 | PT:P2 | 59 | 19 | -5 | 31 | -20 | 1149 | 28 | 39 | -1154
| 36 | 12 | Hurr -50 | 59 | 1 | PT:P3 | 59 | 19 | -5 | 31 | -20 | 1147 | 28 | 39 | -1153
| 36 | 12 | Hurr -50 | 60 | 1 | PT:P4 | 59 | 19 | -5 | 31 | -20 | 1146 | 28 | 39 | -1152
| 37 | 12 | Hurr -45 | 1 | 1 | TL-S1 | 272 | -615 | -6 | 148 | -334 | 3879 | 124 | -280 | -3885
| 37 | 12 | Hurr -45 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 37 | 12 | Hurr -45 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 37 | 12 | Hurr -45 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 37 | 12 | Hurr -45 | 10 | 1 | ST1 | 774 | -1349 | -12 | 401 | -743 | 11978 | 374 | -606 | -11990
| 37 | 12 | Hurr -45 | 10 | 2 | ST2 | 774 | -1354 | -12 | 401 | -744 | 11978 | 374 | -611 | -11990
| 37 | 12 | Hurr -45 | 10 | 3 | ST3 | 774 | -1361 | -12 | 401 | -746 | 11978 | 374 | -615 | -11989
| 37 | 12 | Hurr -45 | 46 | 1 | F2 | 61 | 36 | -3 | 31 | 0 | 725 | 30 | 36 | -728
| 37 | 12 | Hurr -45 | 49 | 1 | S1 | 161 | -458 | -5 | 86 | -256 | 3761 | 75 | -202 | -3766
| 37 | 12 | Hurr -45 | 49 | 2 | S2 | 161 | -460 | -5 | 86 | -257 | 3761 | 75 | -203 | -3766
| 37 | 12 | Hurr -45 | 49 | 3 | S3 | 161 | -463 | -5 | 86 | -258 | 3761 | 75 | -205 | -3765
| 37 | 12 | Hurr -45 | 50 | 1 | S4 | 161 | -425 | -4 | 86 | -237 | 3762 | 75 | -187 | -3766
| 37 | 12 | Hurr -45 | 50 | 2 | S5 | 161 | -426 | -4 | 86 | -238 | 3762 | 75 | -188 | -3766
| 37 | 12 | Hurr -45 | 50 | 3 | S6 | 161 | -428 | -4 | 86 | -238 | 3762 | 75 | -189 | -3766
| 37 | 12 | Hurr -45 | 53 | 1 | S7 | 75 | -49 | -3 | 38 | -41 | 1014 | 37 | -8 | -1017
| 37 | 12 | Hurr -45 | 54 | 1 | S8 | 75 | -39 | -3 | 38 | -35 | 1015 | 37 | -4 | -1018
| 37 | 12 | Hurr -45 | 57 | 1 | PT:P1 | 60 | 32 | -6 | 32 | -15 | 1335 | 28 | 47 | -1341
| 37 | 12 | Hurr -45 | 58 | 1 | PT:P2 | 60 | 32 | -6 | 32 | -15 | 1334 | 28 | 47 | -1339
| 37 | 12 | Hurr -45 | 59 | 1 | PT:P3 | 60 | 32 | -6 | 32 | -15 | 1332 | 28 | 47 | -1338
| 37 | 12 | Hurr -45 | 60 | 1 | PT:P4 | 60 | 32 | -6 | 32 | -15 | 1331 | 28 | 47 | -1336
| 38 | 12 | Hurr -40 | 1 | 1 | TL-S1 | 277 | -604 | -6 | 151 | -330 | 3976 | 126 | -274 | -3982
| 38 | 12 | Hurr -40 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 38 | 12 | Hurr -40 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 38 | 12 | Hurr -40 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 38 | 12 | Hurr -40 | 10 | 1 | ST1 | 779 | -1302 | -13 | 404 | -721 | 12358 | 375 | -581 | -12371
| 38 | 12 | Hurr -40 | 10 | 2 | ST2 | 779 | -1309 | -12 | 404 | -723 | 12358 | 375 | -586 | -12370
| 38 | 12 | Hurr -40 | 10 | 3 | ST3 | 779 | -1317 | -12 | 404 | -726 | 12358 | 375 | -591 | -12370
| 38 | 12 | Hurr -40 | 46 | 1 | F2 | 62 | 47 | -3 | 32 | 4 | 822 | 30 | 42 | -825
| 38 | 12 | Hurr -40 | 49 | 1 | S1 | 162 | -448 | -5 | 86 | -252 | 3913 | 75 | -196 | -3918
| 38 | 12 | Hurr -40 | 49 | 2 | S2 | 162 | -450 | -5 | 86 | -253 | 3913 | 75 | -197 | -3918
| 38 | 12 | Hurr -40 | 49 | 3 | S3 | 162 | -453 | -5 | 86 | -254 | 3913 | 75 | -199 | -3918
| 38 | 12 | Hurr -40 | 50 | 1 | S4 | 161 | -413 | -5 | 86 | -232 | 3915 | 75 | -181 | -3919
| 38 | 12 | Hurr -40 | 50 | 2 | S5 | 161 | -415 | -4 | 86 | -233 | 3914 | 75 | -182 | -3919
| 38 | 12 | Hurr -40 | 50 | 3 | S6 | 161 | -417 | -4 | 86 | -234 | 3914 | 75 | -183 | -3919
| 38 | 12 | Hurr -40 | 53 | 1 | S7 | 76 | -47 | -3 | 39 | -40 | 1129 | 37 | -6 | -1132
| 38 | 12 | Hurr -40 | 54 | 1 | S8 | 76 | -35 | -3 | 39 | -34 | 1130 | 37 | -2 | -1133
| 38 | 12 | Hurr -40 | 57 | 1 | PT:P1 | 61 | 46 | -6 | 33 | -9 | 1515 | 28 | 55 | -1520
| 38 | 12 | Hurr -40 | 58 | 1 | PT:P2 | 61 | 46 | -6 | 33 | -9 | 1513 | 28 | 55 | -1518
| 38 | 12 | Hurr -40 | 59 | 1 | PT:P3 | 61 | 46 | -6 | 33 | -9 | 1511 | 28 | 55 | -1517
| 38 | 12 | Hurr -40 | 60 | 1 | PT:P4 | 61 | 45 | -6 | 33 | -9 | 1509 | 28 | 55 | -1515
| 39 | 12 | Hurr -35 | 1 | 1 | TL-S1 | 281 | -594 | -6 | 153 | -325 | 4072 | 128 | -269 | -4078
| 39 | 12 | Hurr -35 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 39 | 12 | Hurr -35 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 39 | 12 | Hurr -35 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 39 | 12 | Hurr -35 | 10 | 1 | ST1 | 784 | -1262 | -13 | 408 | -702 | 12754 | 376 | -560 | -12767
| 39 | 12 | Hurr -35 | 10 | 2 | ST2 | 784 | -1271 | -12 | 408 | -705 | 12754 | 376 | -566 | -12766
| 39 | 12 | Hurr -35 | 10 | 3 | ST3 | 784 | -1280 | -12 | 408 | -708 | 12754 | 376 | -572 | -12766
| 39 | 12 | Hurr -35 | 46 | 1 | F2 | 62 | 57 | -3 | 32 | 9 | 914 | 30 | 48 | -917
| 39 | 12 | Hurr -35 | 49 | 1 | S1 | 162 | -438 | -5 | 87 | -247 | 4064 | 75 | -191 | -4069
| 39 | 12 | Hurr -35 | 49 | 2 | S2 | 162 | -441 | -5 | 87 | -249 | 4064 | 75 | -193 | -4069
| 39 | 12 | Hurr -35 | 49 | 3 | S3 | 162 | -444 | -5 | 87 | -250 | 4064 | 75 | -194 | -4069
| 39 | 12 | Hurr -35 | 50 | 1 | S4 | 162 | -402 | -5 | 87 | -227 | 4065 | 75 | -175 | -4070
| 39 | 12 | Hurr -35 | 50 | 2 | S5 | 162 | -404 | -5 | 87 | -228 | 4065 | 75 | -176 | -4070
| 39 | 12 | Hurr -35 | 50 | 3 | S6 | 162 | -407 | -4 | 87 | -229 | 4065 | 75 | -178 | -4069
| 39 | 12 | Hurr -35 | 53 | 1 | S7 | 77 | -44 | -3 | 40 | -39 | 1238 | 37 | -5 | -1241
| 39 | 12 | Hurr -35 | 54 | 1 | S8 | 77 | -32 | -3 | 40 | -32 | 1239 | 37 | 0 | -1242
| 39 | 12 | Hurr -35 | 57 | 1 | PT:P1 | 62 | 60 | -6 | 34 | -3 | 1682 | 29 | 63 | -1688
| 39 | 12 | Hurr -35 | 58 | 1 | PT:P2 | 62 | 60 | -6 | 34 | -3 | 1681 | 28 | 63 | -1687
| 39 | 12 | Hurr -35 | 59 | 1 | PT:P3 | 62 | 60 | -6 | 34 | -3 | 1679 | 28 | 62 | -1684
| 39 | 12 | Hurr -35 | 60 | 1 | PT:P4 | 62 | 60 | -6 | 34 | -3 | 1677 | 28 | 62 | -1683
| 40 | 12 | Hurr -30 | 1 | 1 | TL-S1 | 285 | -586 | -6 | 156 | -320 | 4168 | 130 | -266 | -4174
| 40 | 12 | Hurr -30 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 40 | 12 | Hurr -30 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 40 | 12 | Hurr -30 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 40 | 12 | Hurr -30 | 10 | 1 | ST1 | 788 | -1227 | -13 | 411 | -684 | 13135 | 377 | -544 | -13148
| 40 | 12 | Hurr -30 | 10 | 2 | ST2 | 788 | -1237 | -12 | 411 | -687 | 13135 | 377 | -550 | -13147
| 40 | 12 | Hurr -30 | 10 | 3 | ST3 | 788 | -1248 | -12 | 411 | -691 | 13135 | 377 | -557 | -13147
| 40 | 12 | Hurr -30 | 46 | 1 | F2 | 63 | 68 | -3 | 33 | 15 | 997 | 30 | 53 | -1000
| 40 | 12 | Hurr -30 | 49 | 1 | S1 | 163 | -430 | -5 | 88 | -243 | 4208 | 75 | -187 | -4213
| 40 | 12 | Hurr -30 | 49 | 2 | S2 | 163 | -433 | -5 | 88 | -244 | 4208 | 75 | -189 | -4213
| 40 | 12 | Hurr -30 | 49 | 3 | S3 | 163 | -437 | -5 | 88 | -246 | 4207 | 75 | -191 | -4212
| 40 | 12 | Hurr -30 | 50 | 1 | S4 | 163 | -393 | -5 | 88 | -222 | 4209 | 75 | -171 | -4213
| 40 | 12 | Hurr -30 | 50 | 2 | S5 | 163 | -395 | -4 | 88 | -223 | 4209 | 75 | -172 | -4213
| 40 | 12 | Hurr -30 | 50 | 3 | S6 | 163 | -398 | -4 | 88 | -224 | 4209 | 75 | -174 | -4213
| 40 | 12 | Hurr -30 | 53 | 1 | S7 | 77 | -42 | -3 | 40 | -38 | 1339 | 37 | -4 | -1342
| 40 | 12 | Hurr -30 | 54 | 1 | S8 | 77 | -28 | -3 | 40 | -30 | 1340 | 37 | 2 | -1343
| 40 | 12 | Hurr -30 | 57 | 1 | PT:P1 | 63 | 74 | -6 | 35 | 5 | 1835 | 29 | 69 | -1841
| 40 | 12 | Hurr -30 | 58 | 1 | PT:P2 | 63 | 74 | -6 | 35 | 5 | 1834 | 29 | 69 | -1840
| 40 | 12 | Hurr -30 | 59 | 1 | PT:P3 | 63 | 74 | -6 | 35 | 5 | 1832 | 29 | 69 | -1837
| 40 | 12 | Hurr -30 | 60 | 1 | PT:P4 | 63 | 74 | -6 | 35 | 5 | 1830 | 29 | 69 | -1835
| 41 | 12 | Hurr -25 | 1 | 1 | TL-S1 | 289 | -579 | -6 | 158 | -316 | 4256 | 131 | -263 | -4262
| 41 | 12 | Hurr -25 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 41 | 12 | Hurr -25 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 41 | 12 | Hurr -25 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 41 | 12 | Hurr -25 | 10 | 1 | ST1 | 792 | -1197 | -12 | 414 | -666 | 13483 | 378 | -531 | -13495
| 41 | 12 | Hurr -25 | 10 | 2 | ST2 | 792 | -1208 | -12 | 414 | -670 | 13482 | 378 | -538 | -13494
| 41 | 12 | Hurr -25 | 10 | 3 | ST3 | 792 | -1220 | -12 | 414 | -675 | 13482 | 378 | -546 | -13493
| 41 | 12 | Hurr -25 | 46 | 1 | F2 | 63 | 77 | -3 | 33 | 20 | 1071 | 30 | 57 | -1074
| 41 | 12 | Hurr -25 | 49 | 1 | S1 | 163 | -422 | -5 | 88 | -238 | 4337 | 75 | -184 | -4342
| 41 | 12 | Hurr -25 | 49 | 2 | S2 | 163 | -426 | -5 | 88 | -240 | 4337 | 75 | -186 | -4342
| 41 | 12 | Hurr -25 | 49 | 3 | S3 | 163 | -429 | -5 | 88 | -241 | 4337 | 75 | -188 | -4342
| 41 | 12 | Hurr -25 | 50 | 1 | S4 | 163 | -384 | -4 | 88 | -217 | 4338 | 75 | -167 | -4343
| 41 | 12 | Hurr -25 | 50 | 2 | S5 | 163 | -387 | -4 | 88 | -218 | 4338 | 75 | -169 | -4343
| 41 | 12 | Hurr -25 | 50 | 3 | S6 | 163 | -389 | -4 | 88 | -219 | 4338 | 75 | -170 | -4342
| 41 | 12 | Hurr -25 | 53 | 1 | S7 | 78 | -39 | -3 | 41 | -36 | 1428 | 37 | -3 | -1431
| 41 | 12 | Hurr -25 | 54 | 1 | S8 | 78 | -25 | -3 | 41 | -28 | 1428 | 37 | 3 | -1431
| 41 | 12 | Hurr -25 | 57 | 1 | PT:P1 | 64 | 87 | -6 | 35 | 13 | 1971 | 29 | 75 | -1976
| 41 | 12 | Hurr -25 | 58 | 1 | PT:P2 | 64 | 87 | -6 | 35 | 13 | 1969 | 29 | 75 | -1974
| 41 | 12 | Hurr -25 | 59 | 1 | PT:P3 | 64 | 87 | -5 | 35 | 13 | 1966 | 29 | 74 | -1972
| 41 | 12 | Hurr -25 | 60 | 1 | PT:P4 | 64 | 87 | -5 | 35 | 13 | 1964 | 29 | 74 | -1969
| 42 | 12 | Hurr -20 | 1 | 1 | TL-S1 | 292 | -574 | -6 | 160 | -312 | 4335 | 133 | -262 | -4340
| 42 | 12 | Hurr -20 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 42 | 12 | Hurr -20 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 42 | 12 | Hurr -20 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 42 | 12 | Hurr -20 | 10 | 1 | ST1 | 796 | -1172 | -11 | 417 | -649 | 13787 | 379 | -523 | -13799
| 42 | 12 | Hurr -20 | 10 | 2 | ST2 | 796 | -1184 | -11 | 417 | -654 | 13787 | 379 | -530 | -13798
| 42 | 12 | Hurr -20 | 10 | 3 | ST3 | 796 | -1198 | -11 | 417 | -659 | 13786 | 379 | -538 | -13797
| 42 | 12 | Hurr -20 | 46 | 1 | F2 | 64 | 86 | -3 | 34 | 26 | 1133 | 30 | 60 | -1136
| 42 | 12 | Hurr -20 | 49 | 1 | S1 | 164 | -416 | -5 | 89 | -233 | 4450 | 75 | -183 | -4455
| 42 | 12 | Hurr -20 | 49 | 2 | S2 | 164 | -420 | -5 | 89 | -235 | 4450 | 75 | -185 | -4455
| 42 | 12 | Hurr -20 | 49 | 3 | S3 | 164 | -424 | -5 | 89 | -237 | 4450 | 75 | -187 | -4455
| 42 | 12 | Hurr -20 | 50 | 1 | S4 | 163 | -377 | -4 | 89 | -212 | 4452 | 75 | -165 | -4456
| 42 | 12 | Hurr -20 | 50 | 2 | S5 | 163 | -380 | -4 | 89 | -213 | 4451 | 75 | -167 | -4455
| 42 | 12 | Hurr -20 | 50 | 3 | S6 | 163 | -383 | -4 | 89 | -214 | 4451 | 75 | -169 | -4455
| 42 | 12 | Hurr -20 | 53 | 1 | S7 | 78 | -37 | -3 | 41 | -34 | 1504 | 37 | -3 | -1507
| 42 | 12 | Hurr -20 | 54 | 1 | S8 | 78 | -22 | -3 | 41 | -25 | 1505 | 37 | 3 | -1507
| 42 | 12 | Hurr -20 | 57 | 1 | PT:P1 | 65 | 99 | -5 | 36 | 21 | 2085 | 29 | 79 | -2090
| 42 | 12 | Hurr -20 | 58 | 1 | PT:P2 | 65 | 99 | -5 | 36 | 20 | 2083 | 29 | 78 | -2088
| 42 | 12 | Hurr -20 | 59 | 1 | PT:P3 | 65 | 99 | -5 | 36 | 20 | 2080 | 29 | 78 | -2085
| 42 | 12 | Hurr -20 | 60 | 1 | PT:P4 | 65 | 99 | -5 | 36 | 20 | 2078 | 29 | 78 | -2083
| 43 | 12 | Hurr -15 | 1 | 1 | TL-S1 | 295 | -570 | -5 | 162 | -308 | 4400 | 134 | -262 | -4406
| 43 | 12 | Hurr -15 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 43 | 12 | Hurr -15 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 43 | 12 | Hurr -15 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 43 | 12 | Hurr -15 | 10 | 1 | ST1 | 799 | -1153 | -11 | 419 | -634 | 14041 | 380 | -519 | -14051
| 43 | 12 | Hurr -15 | 10 | 2 | ST2 | 799 | -1166 | -10 | 419 | -639 | 14040 | 380 | -527 | -14051
| 43 | 12 | Hurr -15 | 10 | 3 | ST3 | 799 | -1181 | -10 | 419 | -645 | 14040 | 380 | -535 | -14050
| 43 | 12 | Hurr -15 | 46 | 1 | F2 | 64 | 93 | -3 | 34 | 31 | 1182 | 30 | 62 | -1185
| 43 | 12 | Hurr -15 | 49 | 1 | S1 | 164 | -411 | -4 | 89 | -229 | 4540 | 75 | -182 | -4544
| 43 | 12 | Hurr -15 | 49 | 2 | S2 | 164 | -415 | -4 | 89 | -230 | 4540 | 75 | -184 | -4544
| 43 | 12 | Hurr -15 | 49 | 3 | S3 | 164 | -419 | -4 | 89 | -232 | 4540 | 75 | -187 | -4544
| 43 | 12 | Hurr -15 | 50 | 1 | S4 | 164 | -371 | -4 | 89 | -207 | 4541 | 75 | -164 | -4545
| 43 | 12 | Hurr -15 | 50 | 2 | S5 | 164 | -374 | -4 | 89 | -208 | 4541 | 75 | -166 | -4545
| 43 | 12 | Hurr -15 | 50 | 3 | S6 | 164 | -377 | -4 | 89 | -209 | 4541 | 75 | -168 | -4545
| 43 | 12 | Hurr -15 | 53 | 1 | S7 | 79 | -35 | -3 | 42 | -31 | 1564 | 37 | -3 | -1567
| 43 | 12 | Hurr -15 | 54 | 1 | S8 | 79 | -19 | -2 | 42 | -22 | 1565 | 37 | 3 | -1567
| 43 | 12 | Hurr -15 | 57 | 1 | PT:P1 | 65 | 109 | -5 | 37 | 28 | 2177 | 29 | 81 | -2181
| 43 | 12 | Hurr -15 | 58 | 1 | PT:P2 | 65 | 109 | -5 | 36 | 28 | 2174 | 29 | 81 | -2179
| 43 | 12 | Hurr -15 | 59 | 1 | PT:P3 | 65 | 109 | -5 | 36 | 28 | 2171 | 29 | 81 | -2176
| 43 | 12 | Hurr -15 | 60 | 1 | PT:P4 | 65 | 108 | -5 | 36 | 28 | 2169 | 29 | 81 | -2174
| 44 | 12 | Hurr -10 | 1 | 1 | TL-S1 | 297 | -567 | -5 | 163 | -304 | 4449 | 135 | -263 | -4453
| 44 | 12 | Hurr -10 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 44 | 12 | Hurr -10 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 44 | 12 | Hurr -10 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 44 | 12 | Hurr -10 | 10 | 1 | ST1 | 801 | -1139 | -9 | 420 | -620 | 14225 | 381 | -519 | -14234
| 44 | 12 | Hurr -10 | 10 | 2 | ST2 | 801 | -1152 | -9 | 420 | -626 | 14224 | 381 | -527 | -14233
| 44 | 12 | Hurr -10 | 10 | 3 | ST3 | 801 | -1168 | -9 | 420 | -633 | 14224 | 381 | -535 | -14233
| 44 | 12 | Hurr -10 | 46 | 1 | F2 | 64 | 98 | -2 | 34 | 35 | 1219 | 30 | 63 | -1221
| 44 | 12 | Hurr -10 | 49 | 1 | S1 | 165 | -407 | -4 | 90 | -224 | 4605 | 75 | -183 | -4609
| 44 | 12 | Hurr -10 | 49 | 2 | S2 | 165 | -411 | -4 | 90 | -226 | 4605 | 75 | -185 | -4608
| 44 | 12 | Hurr -10 | 49 | 3 | S3 | 165 | -415 | -4 | 90 | -228 | 4605 | 75 | -187 | -4608
| 44 | 12 | Hurr -10 | 50 | 1 | S4 | 164 | -366 | -3 | 89 | -202 | 4606 | 75 | -165 | -4609
| 44 | 12 | Hurr -10 | 50 | 2 | S5 | 164 | -369 | -3 | 89 | -203 | 4606 | 75 | -166 | -4609
| 44 | 12 | Hurr -10 | 50 | 3 | S6 | 164 | -372 | -3 | 89 | -204 | 4606 | 75 | -168 | -4609
| 44 | 12 | Hurr -10 | 53 | 1 | S7 | 79 | -33 | -2 | 42 | -29 | 1609 | 37 | -4 | -1611
| 44 | 12 | Hurr -10 | 54 | 1 | S8 | 79 | -17 | -2 | 42 | -20 | 1609 | 37 | 3 | -1611
| 44 | 12 | Hurr -10 | 57 | 1 | PT:P1 | 66 | 116 | -4 | 37 | 35 | 2243 | 29 | 81 | -2247
| 44 | 12 | Hurr -10 | 58 | 1 | PT:P2 | 66 | 116 | -4 | 37 | 34 | 2240 | 29 | 81 | -2245
| 44 | 12 | Hurr -10 | 59 | 1 | PT:P3 | 66 | 116 | -4 | 37 | 34 | 2238 | 29 | 81 | -2242
| 44 | 12 | Hurr -10 | 60 | 1 | PT:P4 | 65 | 115 | -4 | 37 | 34 | 2235 | 29 | 81 | -2239
| 45 | 12 | Hurr -5 | 1 | 1 | TL-S1 | 299 | -565 | -4 | 164 | -300 | 4475 | 135 | -265 | -4479
| 45 | 12 | Hurr -5 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 45 | 12 | Hurr -5 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 45 | 12 | Hurr -5 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 45 | 12 | Hurr -5 | 10 | 1 | ST1 | 802 | -1130 | -8 | 421 | -608 | 14331 | 381 | -522 | -14339
| 45 | 12 | Hurr -5 | 10 | 2 | ST2 | 802 | -1144 | -8 | 421 | -614 | 14331 | 381 | -530 | -14339
| 45 | 12 | Hurr -5 | 10 | 3 | ST3 | 802 | -1159 | -8 | 421 | -621 | 14330 | 381 | -539 | -14338
| 45 | 12 | Hurr -5 | 46 | 1 | F2 | 64 | 101 | -2 | 34 | 39 | 1241 | 30 | 62 | -1243
| 45 | 12 | Hurr -5 | 49 | 1 | S1 | 165 | -404 | -3 | 90 | -220 | 4645 | 75 | -185 | -4648
| 45 | 12 | Hurr -5 | 49 | 2 | S2 | 165 | -409 | -3 | 90 | -222 | 4644 | 75 | -187 | -4648
| 45 | 12 | Hurr -5 | 49 | 3 | S3 | 165 | -413 | -3 | 90 | -224 | 4644 | 75 | -189 | -4647
| 45 | 12 | Hurr -5 | 50 | 1 | S4 | 164 | -364 | -3 | 90 | -198 | 4646 | 75 | -166 | -4648
| 45 | 12 | Hurr -5 | 50 | 2 | S5 | 164 | -367 | -3 | 90 | -199 | 4645 | 75 | -168 | -4648
| 45 | 12 | Hurr -5 | 50 | 3 | S6 | 164 | -370 | -3 | 90 | -200 | 4645 | 75 | -170 | -4648
| 45 | 12 | Hurr -5 | 53 | 1 | S7 | 79 | -32 | -2 | 42 | -26 | 1635 | 37 | -6 | -1637
| 45 | 12 | Hurr -5 | 54 | 1 | S8 | 79 | -16 | -2 | 42 | -18 | 1636 | 37 | 2 | -1638
| 45 | 12 | Hurr -5 | 57 | 1 | PT:P1 | 66 | 120 | -4 | 37 | 40 | 2283 | 29 | 80 | -2287
| 45 | 12 | Hurr -5 | 58 | 1 | PT:P2 | 66 | 120 | -4 | 37 | 40 | 2280 | 29 | 80 | -2284
| 45 | 12 | Hurr -5 | 59 | 1 | PT:P3 | 66 | 120 | -4 | 37 | 40 | 2278 | 29 | 80 | -2281
| 45 | 12 | Hurr -5 | 60 | 1 | PT:P4 | 66 | 120 | -4 | 37 | 40 | 2275 | 29 | 80 | -2279
| 46 | 12 | Hurr 0 | 1 | 1 | TL-S1 | 299 | -563 | -4 | 164 | -296 | 4475 | 135 | -266 | -4479
| 46 | 12 | Hurr 0 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 46 | 12 | Hurr 0 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 46 | 12 | Hurr 0 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 46 | 12 | Hurr 0 | 10 | 1 | ST1 | 802 | -1121 | -7 | 421 | -595 | 14332 | 381 | -526 | -14339
| 46 | 12 | Hurr 0 | 10 | 2 | ST2 | 802 | -1135 | -6 | 421 | -601 | 14332 | 381 | -534 | -14338
| 46 | 12 | Hurr 0 | 10 | 3 | ST3 | 802 | -1151 | -6 | 421 | -608 | 14331 | 381 | -543 | -14337
| 46 | 12 | Hurr 0 | 46 | 1 | F2 | 64 | 103 | -2 | 34 | 42 | 1241 | 30 | 61 | -1243
| 46 | 12 | Hurr 0 | 49 | 1 | S1 | 165 | -402 | -3 | 90 | -215 | 4645 | 75 | -187 | -4648
| 46 | 12 | Hurr 0 | 49 | 2 | S2 | 165 | -406 | -3 | 90 | -217 | 4645 | 75 | -189 | -4647
| 46 | 12 | Hurr 0 | 49 | 3 | S3 | 165 | -410 | -2 | 90 | -219 | 4645 | 75 | -191 | -4647
| 46 | 12 | Hurr 0 | 50 | 1 | S4 | 164 | -361 | -2 | 90 | -193 | 4646 | 75 | -168 | -4648
| 46 | 12 | Hurr 0 | 50 | 2 | S5 | 164 | -364 | -2 | 90 | -194 | 4646 | 75 | -169 | -4648
| 46 | 12 | Hurr 0 | 50 | 3 | S6 | 164 | -367 | -2 | 90 | -196 | 4646 | 75 | -171 | -4648
| 46 | 12 | Hurr 0 | 53 | 1 | S7 | 79 | -30 | -2 | 42 | -24 | 1636 | 37 | -7 | -1637
| 46 | 12 | Hurr 0 | 54 | 1 | S8 | 79 | -14 | -1 | 42 | -15 | 1636 | 37 | 1 | -1638
| 46 | 12 | Hurr 0 | 57 | 1 | PT:P1 | 66 | 124 | -3 | 37 | 46 | 2283 | 29 | 78 | -2286
| 46 | 12 | Hurr 0 | 58 | 1 | PT:P2 | 66 | 124 | -3 | 37 | 46 | 2281 | 29 | 78 | -2284
| 46 | 12 | Hurr 0 | 59 | 1 | PT:P3 | 66 | 123 | -3 | 37 | 46 | 2278 | 29 | 78 | -2281
| 46 | 12 | Hurr 0 | 60 | 1 | PT:P4 | 66 | 123 | -3 | 37 | 46 | 2276 | 29 | 77 | -2279
| 47 | 12 | Hurr 5 | 1 | 1 | TL-S1 | 299 | -566 | -3 | 164 | -294 | 4476 | 135 | -271 | -4479
| 47 | 12 | Hurr 5 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 47 | 12 | Hurr 5 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 47 | 12 | Hurr 5 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 47 | 12 | Hurr 5 | 10 | 1 | ST1 | 802 | -1132 | -5 | 421 | -591 | 14333 | 381 | -541 | -14338
| 47 | 12 | Hurr 5 | 10 | 2 | ST2 | 802 | -1146 | -5 | 421 | -597 | 14332 | 381 | -548 | -14337
| 47 | 12 | Hurr 5 | 10 | 3 | ST3 | 802 | -1162 | -5 | 421 | -605 | 14331 | 381 | -557 | -14336
| 47 | 12 | Hurr 5 | 46 | 1 | F2 | 64 | 100 | -1 | 34 | 43 | 1241 | 30 | 57 | -1242
| 47 | 12 | Hurr 5 | 49 | 1 | S1 | 165 | -405 | -2 | 90 | -213 | 4645 | 75 | -192 | -4647
| 47 | 12 | Hurr 5 | 49 | 2 | S2 | 165 | -409 | -2 | 90 | -215 | 4645 | 75 | -194 | -4647
| 47 | 12 | Hurr 5 | 49 | 3 | S3 | 165 | -414 | -2 | 90 | -217 | 4645 | 75 | -197 | -4647
| 47 | 12 | Hurr 5 | 50 | 1 | S4 | 164 | -364 | -2 | 90 | -191 | 4646 | 75 | -173 | -4648
| 47 | 12 | Hurr 5 | 50 | 2 | S5 | 164 | -368 | -2 | 90 | -193 | 4646 | 75 | -175 | -4648
| 47 | 12 | Hurr 5 | 50 | 3 | S6 | 164 | -371 | -2 | 90 | -194 | 4646 | 75 | -176 | -4647
| 47 | 12 | Hurr 5 | 53 | 1 | S7 | 79 | -33 | -1 | 42 | -23 | 1636 | 37 | -10 | -1637
| 47 | 12 | Hurr 5 | 54 | 1 | S8 | 79 | -16 | -1 | 42 | -14 | 1636 | 37 | -2 | -1637
| 47 | 12 | Hurr 5 | 57 | 1 | PT:P1 | 66 | 119 | -2 | 37 | 48 | 2284 | 29 | 71 | -2286
| 47 | 12 | Hurr 5 | 58 | 1 | PT:P2 | 66 | 119 | -2 | 37 | 48 | 2281 | 29 | 71 | -2283
| 47 | 12 | Hurr 5 | 59 | 1 | PT:P3 | 66 | 119 | -2 | 37 | 48 | 2278 | 29 | 71 | -2280
| 47 | 12 | Hurr 5 | 60 | 1 | PT:P4 | 66 | 119 | -2 | 37 | 48 | 2276 | 29 | 71 | -2278
| 48 | 12 | Hurr 10 | 1 | 1 | TL-S1 | 297 | -568 | -2 | 163 | -293 | 4450 | 135 | -276 | -4452
| 48 | 12 | Hurr 10 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 48 | 12 | Hurr 10 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 48 | 12 | Hurr 10 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 48 | 12 | Hurr 10 | 10 | 1 | ST1 | 801 | -1141 | -3 | 420 | -587 | 14218 | 381 | -555 | -14221
| 48 | 12 | Hurr 10 | 10 | 2 | ST2 | 801 | -1155 | -3 | 420 | -593 | 14218 | 381 | -562 | -14221
| 48 | 12 | Hurr 10 | 10 | 3 | ST3 | 801 | -1170 | -3 | 420 | -600 | 14217 | 381 | -570 | -14220
| 48 | 12 | Hurr 10 | 46 | 1 | F2 | 64 | 97 | -1 | 34 | 44 | 1220 | 30 | 53 | -1220
| 48 | 12 | Hurr 10 | 49 | 1 | S1 | 165 | -408 | -1 | 90 | -211 | 4606 | 75 | -197 | -4607
| 48 | 12 | Hurr 10 | 49 | 2 | S2 | 165 | -412 | -1 | 90 | -213 | 4606 | 75 | -199 | -4607
| 48 | 12 | Hurr 10 | 49 | 3 | S3 | 165 | -417 | -1 | 90 | -215 | 4606 | 75 | -202 | -4607
| 48 | 12 | Hurr 10 | 50 | 1 | S4 | 164 | -368 | -1 | 89 | -190 | 4607 | 75 | -178 | -4608
| 48 | 12 | Hurr 10 | 50 | 2 | S5 | 164 | -371 | -1 | 89 | -191 | 4607 | 75 | -180 | -4608
| 48 | 12 | Hurr 10 | 50 | 3 | S6 | 164 | -374 | -1 | 89 | -193 | 4607 | 75 | -181 | -4608
| 48 | 12 | Hurr 10 | 53 | 1 | S7 | 79 | -34 | -1 | 42 | -21 | 1610 | 37 | -13 | -1610
| 48 | 12 | Hurr 10 | 54 | 1 | S8 | 79 | -18 | -1 | 42 | -13 | 1610 | 37 | -5 | -1610
| 48 | 12 | Hurr 10 | 57 | 1 | PT:P1 | 66 | 114 | -1 | 37 | 50 | 2244 | 29 | 65 | -2245
| 48 | 12 | Hurr 10 | 58 | 1 | PT:P2 | 66 | 114 | -1 | 37 | 49 | 2242 | 29 | 64 | -2243
| 48 | 12 | Hurr 10 | 59 | 1 | PT:P3 | 66 | 114 | -1 | 37 | 49 | 2239 | 29 | 64 | -2240
| 48 | 12 | Hurr 10 | 60 | 1 | PT:P4 | 65 | 113 | -1 | 37 | 49 | 2236 | 29 | 64 | -2238
| 49 | 12 | Hurr 15 | 1 | 1 | TL-S1 | 295 | -572 | -2 | 162 | -291 | 4402 | 134 | -281 | -4404
| 49 | 12 | Hurr 15 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 49 | 12 | Hurr 15 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 49 | 12 | Hurr 15 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 49 | 12 | Hurr 15 | 10 | 1 | ST1 | 799 | -1159 | -2 | 419 | -586 | 14045 | 380 | -573 | -14047
| 49 | 12 | Hurr 15 | 10 | 2 | ST2 | 799 | -1172 | -2 | 419 | -592 | 14044 | 380 | -580 | -14046
| 49 | 12 | Hurr 15 | 10 | 3 | ST3 | 799 | -1187 | -2 | 419 | -599 | 14044 | 380 | -587 | -14045
| 49 | 12 | Hurr 15 | 46 | 1 | F2 | 64 | 91 | 0 | 34 | 43 | 1184 | 30 | 47 | -1184
| 49 | 12 | Hurr 15 | 49 | 1 | S1 | 164 | -413 | -1 | 89 | -210 | 4542 | 75 | -203 | -4543
| 49 | 12 | Hurr 15 | 49 | 2 | S2 | 164 | -417 | -1 | 89 | -212 | 4542 | 75 | -205 | -4542
| 49 | 12 | Hurr 15 | 49 | 3 | S3 | 164 | -421 | -1 | 89 | -214 | 4542 | 75 | -207 | -4542
| 49 | 12 | Hurr 15 | 50 | 1 | S4 | 164 | -373 | 0 | 89 | -189 | 4543 | 75 | -184 | -4543
| 49 | 12 | Hurr 15 | 50 | 2 | S5 | 164 | -376 | 0 | 89 | -190 | 4543 | 75 | -186 | -4543
| 49 | 12 | Hurr 15 | 50 | 3 | S6 | 164 | -379 | 0 | 89 | -192 | 4543 | 75 | -187 | -4543
| 49 | 12 | Hurr 15 | 53 | 1 | S7 | 79 | -36 | 0 | 42 | -20 | 1566 | 37 | -16 | -1566
| 49 | 12 | Hurr 15 | 54 | 1 | S8 | 79 | -20 | 0 | 42 | -12 | 1565 | 37 | -9 | -1566
| 49 | 12 | Hurr 15 | 57 | 1 | PT:P1 | 65 | 106 | -1 | 37 | 50 | 2178 | 29 | 56 | -2179
| 49 | 12 | Hurr 15 | 58 | 1 | PT:P2 | 65 | 106 | -1 | 37 | 50 | 2176 | 29 | 56 | -2176
| 49 | 12 | Hurr 15 | 59 | 1 | PT:P3 | 65 | 106 | -1 | 36 | 50 | 2173 | 29 | 56 | -2174
| 49 | 12 | Hurr 15 | 60 | 1 | PT:P4 | 65 | 105 | -1 | 36 | 50 | 2171 | 29 | 56 | -2172
| 50 | 12 | Hurr 20 | 1 | 1 | TL-S1 | 293 | -577 | -1 | 160 | -290 | 4341 | 133 | -287 | -4342
| 50 | 12 | Hurr 20 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 50 | 12 | Hurr 20 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 50 | 12 | Hurr 20 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 50 | 12 | Hurr 20 | 10 | 1 | ST1 | 796 | -1180 | 0 | 417 | -587 | 13793 | 379 | -592 | -13793
| 50 | 12 | Hurr 20 | 10 | 2 | ST2 | 796 | -1192 | 0 | 417 | -593 | 13792 | 379 | -599 | -13792
| 50 | 12 | Hurr 20 | 10 | 3 | ST3 | 796 | -1205 | 0 | 417 | -600 | 13791 | 379 | -606 | -13791
| 50 | 12 | Hurr 20 | 46 | 1 | F2 | 64 | 83 | 0 | 34 | 42 | 1134 | 30 | 41 | -1134
| 50 | 12 | Hurr 20 | 49 | 1 | S1 | 164 | -419 | 0 | 89 | -209 | 4453 | 75 | -210 | -4453
| 50 | 12 | Hurr 20 | 49 | 2 | S2 | 164 | -423 | 0 | 89 | -211 | 4452 | 75 | -212 | -4452
| 50 | 12 | Hurr 20 | 49 | 3 | S3 | 164 | -427 | 0 | 89 | -213 | 4452 | 75 | -214 | -4452
| 50 | 12 | Hurr 20 | 50 | 1 | S4 | 163 | -380 | 0 | 89 | -189 | 4453 | 75 | -191 | -4453
| 50 | 12 | Hurr 20 | 50 | 2 | S5 | 163 | -383 | 0 | 89 | -190 | 4453 | 75 | -192 | -4453
| 50 | 12 | Hurr 20 | 50 | 3 | S6 | 163 | -386 | 0 | 89 | -192 | 4453 | 75 | -194 | -4453
| 50 | 12 | Hurr 20 | 53 | 1 | S7 | 78 | -39 | 0 | 41 | -19 | 1505 | 37 | -20 | -1505
| 50 | 12 | Hurr 20 | 54 | 1 | S8 | 78 | -23 | 0 | 41 | -11 | 1505 | 37 | -12 | -1505
| 50 | 12 | Hurr 20 | 57 | 1 | PT:P1 | 65 | 96 | 0 | 36 | 49 | 2087 | 29 | 47 | -2087
| 50 | 12 | Hurr 20 | 58 | 1 | PT:P2 | 65 | 95 | 0 | 36 | 49 | 2085 | 29 | 47 | -2085
| 50 | 12 | Hurr 20 | 59 | 1 | PT:P3 | 65 | 95 | 0 | 36 | 48 | 2083 | 29 | 47 | -2083
| 50 | 12 | Hurr 20 | 60 | 1 | PT:P4 | 65 | 95 | 0 | 36 | 48 | 2081 | 29 | 47 | -2080
| 51 | 12 | Hurr 25 | 1 | 1 | TL-S1 | 289 | -583 | 0 | 158 | -290 | 4263 | 131 | -292 | -4263
| 51 | 12 | Hurr 25 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 51 | 12 | Hurr 25 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 51 | 12 | Hurr 25 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 51 | 12 | Hurr 25 | 10 | 1 | ST1 | 792 | -1206 | 1 | 414 | -592 | 13489 | 378 | -614 | -13488
| 51 | 12 | Hurr 25 | 10 | 2 | ST2 | 792 | -1217 | 1 | 414 | -598 | 13489 | 378 | -620 | -13487
| 51 | 12 | Hurr 25 | 10 | 3 | ST3 | 792 | -1230 | 1 | 414 | -604 | 13488 | 378 | -626 | -13487
| 51 | 12 | Hurr 25 | 46 | 1 | F2 | 63 | 75 | 0 | 33 | 40 | 1072 | 30 | 35 | -1072
| 51 | 12 | Hurr 25 | 49 | 1 | S1 | 163 | -426 | 1 | 88 | -210 | 4342 | 75 | -217 | -4342
| 51 | 12 | Hurr 25 | 49 | 2 | S2 | 163 | -430 | 1 | 88 | -211 | 4342 | 75 | -219 | -4342
| 51 | 12 | Hurr 25 | 49 | 3 | S3 | 163 | -434 | 1 | 88 | -213 | 4342 | 75 | -220 | -4341
| 51 | 12 | Hurr 25 | 50 | 1 | S4 | 163 | -388 | 1 | 88 | -190 | 4341 | 75 | -198 | -4340
| 51 | 12 | Hurr 25 | 50 | 2 | S5 | 163 | -390 | 1 | 88 | -191 | 4341 | 75 | -199 | -4340
| 51 | 12 | Hurr 25 | 50 | 3 | S6 | 163 | -393 | 1 | 88 | -192 | 4340 | 75 | -201 | -4340
| 51 | 12 | Hurr 25 | 53 | 1 | S7 | 78 | -41 | 0 | 41 | -18 | 1430 | 37 | -23 | -1429
| 51 | 12 | Hurr 25 | 54 | 1 | S8 | 78 | -27 | 0 | 41 | -11 | 1430 | 37 | -16 | -1430
| 51 | 12 | Hurr 25 | 57 | 1 | PT:P1 | 64 | 83 | 1 | 35 | 46 | 1974 | 29 | 37 | -1973
| 51 | 12 | Hurr 25 | 58 | 1 | PT:P2 | 64 | 83 | 1 | 35 | 46 | 1972 | 29 | 37 | -1971
| 51 | 12 | Hurr 25 | 59 | 1 | PT:P3 | 64 | 83 | 1 | 35 | 46 | 1969 | 29 | 37 | -1968
| 51 | 12 | Hurr 25 | 60 | 1 | PT:P4 | 64 | 83 | 1 | 35 | 46 | 1967 | 29 | 37 | -1966
| 52 | 12 | Hurr 30 | 1 | 1 | TL-S1 | 285 | -589 | 0 | 156 | -291 | 4171 | 130 | -298 | -4171
| 52 | 12 | Hurr 30 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 52 | 12 | Hurr 30 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 52 | 12 | Hurr 30 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 52 | 12 | Hurr 30 | 10 | 1 | ST1 | 788 | -1238 | 3 | 411 | -600 | 13143 | 377 | -638 | -13140
| 52 | 12 | Hurr 30 | 10 | 2 | ST2 | 788 | -1248 | 3 | 411 | -605 | 13142 | 377 | -642 | -13139
| 52 | 12 | Hurr 30 | 10 | 3 | ST3 | 788 | -1259 | 3 | 411 | -611 | 13142 | 377 | -648 | -13139
| 52 | 12 | Hurr 30 | 46 | 1 | F2 | 63 | 65 | 1 | 33 | 37 | 999 | 30 | 28 | -998
| 52 | 12 | Hurr 30 | 49 | 1 | S1 | 163 | -434 | 1 | 88 | -210 | 4211 | 75 | -224 | -4209
| 52 | 12 | Hurr 30 | 49 | 2 | S2 | 163 | -437 | 1 | 88 | -212 | 4211 | 75 | -225 | -4209
| 52 | 12 | Hurr 30 | 49 | 3 | S3 | 163 | -441 | 1 | 88 | -214 | 4210 | 75 | -227 | -4209
| 52 | 12 | Hurr 30 | 50 | 1 | S4 | 163 | -397 | 1 | 88 | -191 | 4212 | 75 | -205 | -4210
| 52 | 12 | Hurr 30 | 50 | 2 | S5 | 163 | -399 | 1 | 88 | -193 | 4211 | 75 | -207 | -4210
| 52 | 12 | Hurr 30 | 50 | 3 | S6 | 163 | -402 | 1 | 88 | -194 | 4211 | 75 | -208 | -4210
| 52 | 12 | Hurr 30 | 53 | 1 | S7 | 77 | -44 | 1 | 40 | -18 | 1341 | 37 | -26 | -1341
| 52 | 12 | Hurr 30 | 54 | 1 | S8 | 77 | -31 | 1 | 40 | -11 | 1341 | 37 | -19 | -1340
| 52 | 12 | Hurr 30 | 57 | 1 | PT:P1 | 63 | 69 | 1 | 35 | 43 | 1839 | 29 | 26 | -1837
| 52 | 12 | Hurr 30 | 58 | 1 | PT:P2 | 63 | 69 | 1 | 35 | 43 | 1837 | 29 | 26 | -1836
| 52 | 12 | Hurr 30 | 59 | 1 | PT:P3 | 63 | 69 | 1 | 35 | 43 | 1835 | 29 | 26 | -1834
| 52 | 12 | Hurr 30 | 60 | 1 | PT:P4 | 63 | 69 | 1 | 35 | 43 | 1833 | 28 | 26 | -1832
| 53 | 12 | Hurr 35 | 1 | 1 | TL-S1 | 281 | -598 | 1 | 153 | -293 | 4079 | 128 | -305 | -4079
| 53 | 12 | Hurr 35 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 53 | 12 | Hurr 35 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 53 | 12 | Hurr 35 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 53 | 12 | Hurr 35 | 10 | 1 | ST1 | 784 | -1274 | 4 | 408 | -612 | 12762 | 376 | -662 | -12758
| 53 | 12 | Hurr 35 | 10 | 2 | ST2 | 784 | -1282 | 4 | 408 | -616 | 12762 | 376 | -666 | -12758
| 53 | 12 | Hurr 35 | 10 | 3 | ST3 | 784 | -1292 | 4 | 408 | -621 | 12761 | 376 | -670 | -12757
| 53 | 12 | Hurr 35 | 46 | 1 | F2 | 62 | 54 | 1 | 32 | 34 | 915 | 30 | 20 | -914
| 53 | 12 | Hurr 35 | 49 | 1 | S1 | 162 | -443 | 2 | 87 | -212 | 4067 | 75 | -231 | -4065
| 53 | 12 | Hurr 35 | 49 | 2 | S2 | 162 | -446 | 2 | 87 | -214 | 4067 | 75 | -232 | -4065
| 53 | 12 | Hurr 35 | 49 | 3 | S3 | 162 | -449 | 2 | 87 | -215 | 4067 | 75 | -233 | -4065
| 53 | 12 | Hurr 35 | 50 | 1 | S4 | 162 | -407 | 2 | 87 | -194 | 4068 | 75 | -213 | -4066
| 53 | 12 | Hurr 35 | 50 | 2 | S5 | 162 | -409 | 2 | 87 | -195 | 4068 | 75 | -214 | -4066
| 53 | 12 | Hurr 35 | 50 | 3 | S6 | 162 | -411 | 2 | 87 | -196 | 4068 | 75 | -215 | -4066
| 53 | 12 | Hurr 35 | 53 | 1 | S7 | 77 | -47 | 1 | 40 | -18 | 1241 | 37 | -29 | -1240
| 53 | 12 | Hurr 35 | 54 | 1 | S8 | 77 | -35 | 1 | 40 | -12 | 1241 | 37 | -23 | -1240
| 53 | 12 | Hurr 35 | 57 | 1 | PT:P1 | 62 | 55 | 2 | 34 | 39 | 1686 | 28 | 16 | -1684
| 53 | 12 | Hurr 35 | 58 | 1 | PT:P2 | 62 | 55 | 2 | 34 | 38 | 1684 | 28 | 16 | -1682
| 53 | 12 | Hurr 35 | 59 | 1 | PT:P3 | 62 | 54 | 2 | 34 | 38 | 1682 | 28 | 16 | -1680
| 53 | 12 | Hurr 35 | 60 | 1 | PT:P4 | 62 | 54 | 2 | 34 | 38 | 1681 | 28 | 16 | -1679
| 54 | 12 | Hurr 40 | 1 | 1 | TL-S1 | 277 | -607 | 1 | 151 | -296 | 3979 | 126 | -311 | -3978
| 54 | 12 | Hurr 40 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 54 | 12 | Hurr 40 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 54 | 12 | Hurr 40 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 54 | 12 | Hurr 40 | 10 | 1 | ST1 | 779 | -1314 | 5 | 404 | -627 | 12367 | 375 | -688 | -12362
| 54 | 12 | Hurr 40 | 10 | 2 | ST2 | 779 | -1321 | 5 | 404 | -631 | 12366 | 375 | -691 | -12361
| 54 | 12 | Hurr 40 | 10 | 3 | ST3 | 779 | -1329 | 5 | 404 | -635 | 12366 | 375 | -694 | -12361
| 54 | 12 | Hurr 40 | 46 | 1 | F2 | 62 | 43 | 1 | 32 | 30 | 824 | 30 | 14 | -823
| 54 | 12 | Hurr 40 | 49 | 1 | S1 | 162 | -452 | 2 | 86 | -215 | 3917 | 75 | -237 | -3915
| 54 | 12 | Hurr 40 | 49 | 2 | S2 | 162 | -455 | 2 | 86 | -216 | 3917 | 75 | -239 | -3914
| 54 | 12 | Hurr 40 | 49 | 3 | S3 | 162 | -458 | 2 | 86 | -218 | 3916 | 75 | -240 | -3914
| 54 | 12 | Hurr 40 | 50 | 1 | S4 | 161 | -418 | 2 | 86 | -198 | 3917 | 75 | -220 | -3916
| 54 | 12 | Hurr 40 | 50 | 2 | S5 | 161 | -420 | 2 | 86 | -199 | 3917 | 75 | -221 | -3916
| 54 | 12 | Hurr 40 | 50 | 3 | S6 | 161 | -421 | 2 | 86 | -199 | 3917 | 75 | -222 | -3915
| 54 | 12 | Hurr 40 | 53 | 1 | S7 | 76 | -50 | 1 | 39 | -18 | 1132 | 37 | -32 | -1131
| 54 | 12 | Hurr 40 | 54 | 1 | S8 | 76 | -38 | 1 | 39 | -12 | 1131 | 37 | -26 | -1130
| 54 | 12 | Hurr 40 | 57 | 1 | PT:P1 | 61 | 40 | 2 | 33 | 34 | 1518 | 28 | 7 | -1516
| 54 | 12 | Hurr 40 | 58 | 1 | PT:P2 | 61 | 40 | 2 | 33 | 34 | 1516 | 28 | 7 | -1514
| 54 | 12 | Hurr 40 | 59 | 1 | PT:P3 | 61 | 40 | 2 | 33 | 34 | 1515 | 28 | 7 | -1512
| 54 | 12 | Hurr 40 | 60 | 1 | PT:P4 | 61 | 40 | 2 | 33 | 33 | 1513 | 28 | 6 | -1511
| 55 | 12 | Hurr 45 | 1 | 1 | TL-S1 | 272 | -619 | 1 | 148 | -301 | 3887 | 124 | -318 | -3886
| 55 | 12 | Hurr 45 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 55 | 12 | Hurr 45 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 55 | 12 | Hurr 45 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 55 | 12 | Hurr 45 | 10 | 1 | ST1 | 774 | -1361 | 6 | 401 | -646 | 11986 | 374 | -715 | -11981
| 55 | 12 | Hurr 45 | 10 | 2 | ST2 | 774 | -1367 | 6 | 401 | -650 | 11986 | 374 | -717 | -11981
| 55 | 12 | Hurr 45 | 10 | 3 | ST3 | 774 | -1373 | 5 | 401 | -653 | 11986 | 374 | -720 | -11980
| 55 | 12 | Hurr 45 | 46 | 1 | F2 | 61 | 33 | 2 | 31 | 25 | 727 | 30 | 7 | -725
| 55 | 12 | Hurr 45 | 49 | 1 | S1 | 161 | -463 | 2 | 86 | -219 | 3764 | 75 | -244 | -3762
| 55 | 12 | Hurr 45 | 49 | 2 | S2 | 161 | -465 | 2 | 86 | -220 | 3764 | 75 | -245 | -3762
| 55 | 12 | Hurr 45 | 49 | 3 | S3 | 161 | -467 | 2 | 86 | -221 | 3764 | 75 | -246 | -3762
| 55 | 12 | Hurr 45 | 50 | 1 | S4 | 161 | -430 | 2 | 86 | -202 | 3765 | 75 | -228 | -3763
| 55 | 12 | Hurr 45 | 50 | 2 | S5 | 161 | -431 | 2 | 86 | -203 | 3765 | 75 | -228 | -3763
| 55 | 12 | Hurr 45 | 50 | 3 | S6 | 161 | -432 | 2 | 86 | -204 | 3765 | 75 | -229 | -3763
| 55 | 12 | Hurr 45 | 53 | 1 | S7 | 75 | -52 | 1 | 38 | -18 | 1017 | 37 | -34 | -1015
| 55 | 12 | Hurr 45 | 54 | 1 | S8 | 75 | -41 | 1 | 38 | -13 | 1016 | 37 | -28 | -1015
| 55 | 12 | Hurr 45 | 57 | 1 | PT:P1 | 60 | 26 | 3 | 32 | 28 | 1339 | 28 | -2 | -1337
| 55 | 12 | Hurr 45 | 58 | 1 | PT:P2 | 60 | 26 | 3 | 32 | 28 | 1338 | 28 | -2 | -1335
| 55 | 12 | Hurr 45 | 59 | 1 | PT:P3 | 60 | 26 | 3 | 32 | 28 | 1336 | 28 | -2 | -1334
| 55 | 12 | Hurr 45 | 60 | 1 | PT:P4 | 60 | 26 | 3 | 32 | 28 | 1335 | 28 | -2 | -1332
| 56 | 12 | Hurr 50 | 1 | 1 | TL-S1 | 269 | -632 | 1 | 146 | -306 | 3799 | 123 | -325 | -3798
| 56 | 12 | Hurr 50 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 56 | 12 | Hurr 50 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 56 | 12 | Hurr 50 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 56 | 12 | Hurr 50 | 10 | 1 | ST1 | 770 | -1412 | 6 | 398 | -670 | 11622 | 373 | -743 | -11616
| 56 | 12 | Hurr 50 | 10 | 2 | ST2 | 770 | -1416 | 6 | 398 | -672 | 11622 | 373 | -744 | -11616
| 56 | 12 | Hurr 50 | 10 | 3 | ST3 | 770 | -1421 | 6 | 398 | -675 | 11622 | 373 | -746 | -11616
| 56 | 12 | Hurr 50 | 46 | 1 | F2 | 61 | 23 | 2 | 31 | 21 | 626 | 30 | 2 | -625
| 56 | 12 | Hurr 50 | 49 | 1 | S1 | 161 | -475 | 2 | 85 | -224 | 3620 | 76 | -251 | -3618
| 56 | 12 | Hurr 50 | 49 | 2 | S2 | 161 | -477 | 2 | 85 | -225 | 3620 | 76 | -252 | -3618
| 56 | 12 | Hurr 50 | 49 | 3 | S3 | 161 | -479 | 2 | 85 | -226 | 3620 | 76 | -253 | -3618
| 56 | 12 | Hurr 50 | 50 | 1 | S4 | 160 | -443 | 2 | 85 | -208 | 3621 | 75 | -235 | -3619
| 56 | 12 | Hurr 50 | 50 | 2 | S5 | 160 | -444 | 2 | 85 | -208 | 3621 | 75 | -235 | -3619
| 56 | 12 | Hurr 50 | 50 | 3 | S6 | 160 | -445 | 2 | 85 | -209 | 3621 | 75 | -236 | -3619
| 56 | 12 | Hurr 50 | 53 | 1 | S7 | 75 | -53 | 2 | 38 | -18 | 900 | 37 | -35 | -899
| 56 | 12 | Hurr 50 | 54 | 1 | S8 | 74 | -44 | 1 | 38 | -14 | 900 | 37 | -30 | -898
| 56 | 12 | Hurr 50 | 57 | 1 | PT:P1 | 59 | 14 | 3 | 31 | 23 | 1154 | 28 | -9 | -1151
| 56 | 12 | Hurr 50 | 58 | 1 | PT:P2 | 59 | 14 | 3 | 31 | 23 | 1153 | 28 | -9 | -1150
| 56 | 12 | Hurr 50 | 59 | 1 | PT:P3 | 59 | 14 | 3 | 31 | 23 | 1151 | 28 | -9 | -1148
| 56 | 12 | Hurr 50 | 60 | 1 | PT:P4 | 59 | 14 | 3 | 31 | 23 | 1150 | 28 | -9 | -1147
| 57 | 12 | Hurr 55 | 1 | 1 | TL-S1 | 265 | -647 | 1 | 144 | -314 | 3728 | 121 | -333 | -3727
| 57 | 12 | Hurr 55 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 57 | 12 | Hurr 55 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 57 | 12 | Hurr 55 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 57 | 12 | Hurr 55 | 10 | 1 | ST1 | 767 | -1471 | 6 | 395 | -698 | 11317 | 372 | -773 | -11311
| 57 | 12 | Hurr 55 | 10 | 2 | ST2 | 767 | -1473 | 6 | 395 | -700 | 11317 | 372 | -773 | -11311
| 57 | 12 | Hurr 55 | 10 | 3 | ST3 | 767 | -1476 | 6 | 395 | -702 | 11317 | 372 | -774 | -11311
| 57 | 12 | Hurr 55 | 46 | 1 | F2 | 60 | 14 | 2 | 30 | 17 | 526 | 30 | -3 | -524
| 57 | 12 | Hurr 55 | 49 | 1 | S1 | 160 | -488 | 2 | 85 | -230 | 3491 | 76 | -258 | -3489
| 57 | 12 | Hurr 55 | 49 | 2 | S2 | 160 | -490 | 2 | 85 | -231 | 3491 | 76 | -258 | -3488
| 57 | 12 | Hurr 55 | 49 | 3 | S3 | 160 | -491 | 2 | 85 | -232 | 3491 | 76 | -259 | -3488
| 57 | 12 | Hurr 55 | 50 | 1 | S4 | 160 | -457 | 2 | 84 | -215 | 3492 | 75 | -242 | -3490
| 57 | 12 | Hurr 55 | 50 | 2 | S5 | 160 | -458 | 2 | 84 | -215 | 3492 | 75 | -243 | -3490
| 57 | 12 | Hurr 55 | 50 | 3 | S6 | 160 | -459 | 2 | 84 | -216 | 3492 | 75 | -243 | -3490
| 57 | 12 | Hurr 55 | 53 | 1 | S7 | 74 | -55 | 2 | 37 | -19 | 787 | 37 | -36 | -785
| 57 | 12 | Hurr 55 | 54 | 1 | S8 | 74 | -47 | 1 | 37 | -15 | 786 | 37 | -32 | -785
| 57 | 12 | Hurr 55 | 57 | 1 | PT:P1 | 58 | 3 | 3 | 30 | 18 | 968 | 28 | -15 | -965
| 57 | 12 | Hurr 55 | 58 | 1 | PT:P2 | 58 | 3 | 3 | 30 | 18 | 967 | 28 | -15 | -964
| 57 | 12 | Hurr 55 | 59 | 1 | PT:P3 | 58 | 3 | 3 | 30 | 18 | 966 | 28 | -15 | -963
| 57 | 12 | Hurr 55 | 60 | 1 | PT:P4 | 58 | 3 | 3 | 30 | 18 | 964 | 28 | -15 | -961
| 58 | 12 | Hurr 60 | 1 | 1 | TL-S1 | 263 | -663 | 1 | 143 | -322 | 3671 | 120 | -341 | -3670
| 58 | 12 | Hurr 60 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 58 | 12 | Hurr 60 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 58 | 12 | Hurr 60 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 58 | 12 | Hurr 60 | 10 | 1 | ST1 | 764 | -1535 | 6 | 393 | -731 | 11072 | 371 | -803 | -11066
| 58 | 12 | Hurr 60 | 10 | 2 | ST2 | 764 | -1536 | 6 | 393 | -732 | 11072 | 371 | -803 | -11066
| 58 | 12 | Hurr 60 | 10 | 3 | ST3 | 764 | -1537 | 6 | 393 | -733 | 11072 | 371 | -803 | -11066
| 58 | 12 | Hurr 60 | 46 | 1 | F2 | 59 | 6 | 2 | 30 | 12 | 429 | 30 | -7 | -428
| 58 | 12 | Hurr 60 | 49 | 1 | S1 | 160 | -503 | 2 | 84 | -238 | 3382 | 76 | -265 | -3380
| 58 | 12 | Hurr 60 | 49 | 2 | S2 | 160 | -504 | 2 | 84 | -239 | 3382 | 76 | -265 | -3379
| 58 | 12 | Hurr 60 | 49 | 3 | S3 | 160 | -505 | 2 | 84 | -240 | 3382 | 76 | -266 | -3379
| 58 | 12 | Hurr 60 | 50 | 1 | S4 | 159 | -473 | 2 | 84 | -223 | 3383 | 75 | -250 | -3381
| 58 | 12 | Hurr 60 | 50 | 2 | S5 | 159 | -473 | 2 | 84 | -223 | 3383 | 75 | -250 | -3381
| 58 | 12 | Hurr 60 | 50 | 3 | S6 | 159 | -474 | 2 | 84 | -224 | 3383 | 75 | -250 | -3381
| 58 | 12 | Hurr 60 | 53 | 1 | S7 | 73 | -57 | 2 | 37 | -20 | 683 | 37 | -37 | -681
| 58 | 12 | Hurr 60 | 54 | 1 | S8 | 73 | -50 | 1 | 37 | -17 | 683 | 37 | -33 | -681
| 58 | 12 | Hurr 60 | 57 | 1 | PT:P1 | 57 | -7 | 3 | 29 | 13 | 788 | 28 | -19 | -785
| 58 | 12 | Hurr 60 | 58 | 1 | PT:P2 | 57 | -7 | 3 | 29 | 13 | 787 | 28 | -19 | -784
| 58 | 12 | Hurr 60 | 59 | 1 | PT:P3 | 57 | -7 | 3 | 29 | 13 | 786 | 28 | -19 | -783
| 58 | 12 | Hurr 60 | 60 | 1 | PT:P4 | 57 | -7 | 3 | 29 | 13 | 785 | 28 | -19 | -782
| 59 | 12 | Hurr 65 | 1 | 1 | TL-S1 | 261 | -680 | 1 | 141 | -332 | 3626 | 120 | -348 | -3625
| 59 | 12 | Hurr 65 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 59 | 12 | Hurr 65 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 59 | 12 | Hurr 65 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 59 | 12 | Hurr 65 | 10 | 1 | ST1 | 762 | -1601 | 6 | 391 | -767 | 10889 | 370 | -834 | -10884
| 59 | 12 | Hurr 65 | 10 | 2 | ST2 | 761 | -1600 | 6 | 391 | -767 | 10889 | 370 | -833 | -10884
| 59 | 12 | Hurr 65 | 10 | 3 | ST3 | 761 | -1600 | 6 | 391 | -768 | 10889 | 370 | -833 | -10884
| 59 | 12 | Hurr 65 | 46 | 1 | F2 | 59 | -2 | 1 | 29 | 8 | 343 | 30 | -10 | -341
| 59 | 12 | Hurr 65 | 49 | 1 | S1 | 159 | -520 | 2 | 84 | -248 | 3305 | 76 | -272 | -3302
| 59 | 12 | Hurr 65 | 49 | 2 | S2 | 159 | -521 | 2 | 84 | -248 | 3305 | 76 | -273 | -3302
| 59 | 12 | Hurr 65 | 49 | 3 | S3 | 159 | -522 | 2 | 84 | -249 | 3305 | 76 | -273 | -3302
| 59 | 12 | Hurr 65 | 50 | 1 | S4 | 159 | -490 | 2 | 84 | -233 | 3306 | 75 | -258 | -3304
| 59 | 12 | Hurr 65 | 50 | 2 | S5 | 159 | -491 | 2 | 84 | -233 | 3306 | 75 | -258 | -3304
| 59 | 12 | Hurr 65 | 50 | 3 | S6 | 159 | -491 | 2 | 84 | -233 | 3306 | 75 | -258 | -3304
| 59 | 12 | Hurr 65 | 53 | 1 | S7 | 73 | -60 | 1 | 36 | -22 | 595 | 37 | -38 | -594
| 59 | 12 | Hurr 65 | 54 | 1 | S8 | 73 | -54 | 1 | 36 | -20 | 595 | 37 | -34 | -594
| 59 | 12 | Hurr 65 | 57 | 1 | PT:P1 | 56 | -14 | 3 | 28 | 8 | 622 | 28 | -22 | -620
| 59 | 12 | Hurr 65 | 58 | 1 | PT:P2 | 56 | -14 | 3 | 28 | 8 | 622 | 28 | -22 | -619
| 59 | 12 | Hurr 65 | 59 | 1 | PT:P3 | 56 | -14 | 3 | 28 | 8 | 621 | 28 | -22 | -619
| 59 | 12 | Hurr 65 | 60 | 1 | PT:P4 | 56 | -14 | 3 | 28 | 8 | 620 | 28 | -22 | -618
| 60 | 12 | Hurr 70 | 1 | 1 | TL-S1 | 260 | -697 | 1 | 141 | -342 | 3604 | 119 | -355 | -3603
| 60 | 12 | Hurr 70 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 60 | 12 | Hurr 70 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 60 | 12 | Hurr 70 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 60 | 12 | Hurr 70 | 10 | 1 | ST1 | 760 | -1669 | 5 | 390 | -805 | 10780 | 370 | -864 | -10775
| 60 | 12 | Hurr 70 | 10 | 2 | ST2 | 760 | -1667 | 5 | 390 | -805 | 10780 | 370 | -863 | -10775
| 60 | 12 | Hurr 70 | 10 | 3 | ST3 | 760 | -1666 | 5 | 390 | -804 | 10780 | 370 | -862 | -10775
| 60 | 12 | Hurr 70 | 46 | 1 | F2 | 59 | -9 | 1 | 29 | 3 | 272 | 30 | -12 | -271
| 60 | 12 | Hurr 70 | 49 | 1 | S1 | 159 | -537 | 2 | 83 | -258 | 3254 | 76 | -279 | -3252
| 60 | 12 | Hurr 70 | 49 | 2 | S2 | 159 | -538 | 2 | 83 | -258 | 3254 | 76 | -280 | -3252
| 60 | 12 | Hurr 70 | 49 | 3 | S3 | 159 | -539 | 2 | 83 | -259 | 3254 | 76 | -280 | -3252
| 60 | 12 | Hurr 70 | 50 | 1 | S4 | 159 | -508 | 2 | 83 | -243 | 3256 | 75 | -265 | -3254
| 60 | 12 | Hurr 70 | 50 | 2 | S5 | 159 | -508 | 2 | 83 | -243 | 3256 | 75 | -265 | -3254
| 60 | 12 | Hurr 70 | 50 | 3 | S6 | 159 | -508 | 2 | 83 | -243 | 3256 | 75 | -265 | -3254
| 60 | 12 | Hurr 70 | 53 | 1 | S7 | 72 | -64 | 1 | 36 | -26 | 532 | 37 | -39 | -531
| 60 | 12 | Hurr 70 | 54 | 1 | S8 | 72 | -59 | 1 | 36 | -23 | 532 | 37 | -36 | -531
| 60 | 12 | Hurr 70 | 57 | 1 | PT:P1 | 55 | -22 | 2 | 27 | 2 | 485 | 28 | -24 | -483
| 60 | 12 | Hurr 70 | 58 | 1 | PT:P2 | 55 | -22 | 2 | 27 | 2 | 485 | 28 | -24 | -482
| 60 | 12 | Hurr 70 | 59 | 1 | PT:P3 | 55 | -22 | 2 | 27 | 2 | 484 | 28 | -24 | -482
| 60 | 12 | Hurr 70 | 60 | 1 | PT:P4 | 55 | -22 | 2 | 27 | 2 | 484 | 28 | -24 | -482
| 61 | 12 | Hurr 75 | 1 | 1 | TL-S1 | 259 | -712 | 1 | 141 | -351 | 3590 | 119 | -361 | -3589
| 61 | 12 | Hurr 75 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 61 | 12 | Hurr 75 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 61 | 12 | Hurr 75 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 61 | 12 | Hurr 75 | 10 | 1 | ST1 | 760 | -1735 | 4 | 390 | -844 | 10735 | 370 | -891 | -10731
| 61 | 12 | Hurr 75 | 10 | 2 | ST2 | 760 | -1732 | 4 | 390 | -843 | 10735 | 370 | -890 | -10731
| 61 | 12 | Hurr 75 | 10 | 3 | ST3 | 760 | -1730 | 4 | 390 | -842 | 10735 | 370 | -888 | -10731
| 61 | 12 | Hurr 75 | 46 | 1 | F2 | 58 | -16 | 1 | 28 | -2 | 226 | 30 | -14 | -225
| 61 | 12 | Hurr 75 | 49 | 1 | S1 | 159 | -554 | 2 | 83 | -268 | 3226 | 76 | -285 | -3224
| 61 | 12 | Hurr 75 | 49 | 2 | S2 | 159 | -554 | 2 | 83 | -269 | 3226 | 76 | -286 | -3224
| 61 | 12 | Hurr 75 | 49 | 3 | S3 | 159 | -555 | 2 | 83 | -269 | 3226 | 76 | -286 | -3224
| 61 | 12 | Hurr 75 | 50 | 1 | S4 | 159 | -525 | 2 | 83 | -254 | 3227 | 75 | -271 | -3226
| 61 | 12 | Hurr 75 | 50 | 2 | S5 | 159 | -525 | 2 | 83 | -254 | 3227 | 75 | -271 | -3226
| 61 | 12 | Hurr 75 | 50 | 3 | S6 | 159 | -525 | 2 | 83 | -254 | 3227 | 75 | -271 | -3226
| 61 | 12 | Hurr 75 | 53 | 1 | S7 | 72 | -71 | 1 | 36 | -30 | 494 | 37 | -41 | -493
| 61 | 12 | Hurr 75 | 54 | 1 | S8 | 72 | -66 | 1 | 36 | -28 | 494 | 36 | -38 | -493
| 61 | 12 | Hurr 75 | 57 | 1 | PT:P1 | 54 | -31 | 2 | 26 | -5 | 390 | 28 | -26 | -388
| 61 | 12 | Hurr 75 | 58 | 1 | PT:P2 | 54 | -31 | 2 | 26 | -5 | 389 | 28 | -26 | -388
| 61 | 12 | Hurr 75 | 59 | 1 | PT:P3 | 54 | -31 | 2 | 26 | -5 | 389 | 28 | -26 | -387
| 61 | 12 | Hurr 75 | 60 | 1 | PT:P4 | 54 | -31 | 2 | 26 | -5 | 389 | 28 | -26 | -387
| 62 | 12 | Hurr 80 | 1 | 1 | TL-S1 | 259 | -725 | 0 | 140 | -360 | 3585 | 119 | -365 | -3584
| 62 | 12 | Hurr 80 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 62 | 12 | Hurr 80 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 62 | 12 | Hurr 80 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 62 | 12 | Hurr 80 | 10 | 1 | ST1 | 759 | -1789 | 3 | 390 | -878 | 10711 | 370 | -912 | -10708
| 62 | 12 | Hurr 80 | 10 | 2 | ST2 | 759 | -1786 | 3 | 390 | -876 | 10711 | 370 | -910 | -10708
| 62 | 12 | Hurr 80 | 10 | 3 | ST3 | 759 | -1783 | 3 | 390 | -875 | 10711 | 370 | -908 | -10708
| 62 | 12 | Hurr 80 | 46 | 1 | F2 | 58 | -24 | 1 | 28 | -8 | 204 | 30 | -16 | -203
| 62 | 12 | Hurr 80 | 49 | 1 | S1 | 159 | -567 | 1 | 83 | -278 | 3214 | 76 | -290 | -3213
| 62 | 12 | Hurr 80 | 49 | 2 | S2 | 159 | -568 | 1 | 83 | -278 | 3214 | 76 | -290 | -3213
| 62 | 12 | Hurr 80 | 49 | 3 | S3 | 159 | -568 | 1 | 83 | -278 | 3214 | 76 | -290 | -3213
| 62 | 12 | Hurr 80 | 50 | 1 | S4 | 159 | -539 | 1 | 83 | -263 | 3215 | 75 | -276 | -3214
| 62 | 12 | Hurr 80 | 50 | 2 | S5 | 159 | -538 | 1 | 83 | -263 | 3215 | 75 | -276 | -3214
| 62 | 12 | Hurr 80 | 50 | 3 | S6 | 159 | -538 | 1 | 83 | -263 | 3215 | 75 | -275 | -3214
| 62 | 12 | Hurr 80 | 53 | 1 | S7 | 72 | -77 | 1 | 35 | -35 | 478 | 37 | -42 | -478
| 62 | 12 | Hurr 80 | 54 | 1 | S8 | 72 | -73 | 1 | 35 | -33 | 478 | 36 | -40 | -478
| 62 | 12 | Hurr 80 | 57 | 1 | PT:P1 | 54 | -42 | 1 | 26 | -13 | 342 | 28 | -28 | -341
| 62 | 12 | Hurr 80 | 58 | 1 | PT:P2 | 54 | -42 | 1 | 26 | -13 | 342 | 28 | -28 | -341
| 62 | 12 | Hurr 80 | 59 | 1 | PT:P3 | 54 | -42 | 1 | 26 | -13 | 342 | 28 | -28 | -341
| 62 | 12 | Hurr 80 | 60 | 1 | PT:P4 | 54 | -42 | 1 | 26 | -13 | 342 | 28 | -28 | -341
| 63 | 12 | Hurr 85 | 1 | 1 | TL-S1 | 259 | -733 | 0 | 140 | -367 | 3584 | 119 | -366 | -3584
| 63 | 12 | Hurr 85 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 63 | 12 | Hurr 85 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 63 | 12 | Hurr 85 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 63 | 12 | Hurr 85 | 10 | 1 | ST1 | 759 | -1831 | 2 | 390 | -906 | 10709 | 370 | -925 | -10708
| 63 | 12 | Hurr 85 | 10 | 2 | ST2 | 759 | -1827 | 2 | 390 | -904 | 10709 | 370 | -923 | -10708
| 63 | 12 | Hurr 85 | 10 | 3 | ST3 | 759 | -1824 | 2 | 390 | -903 | 10710 | 370 | -921 | -10708
| 63 | 12 | Hurr 85 | 46 | 1 | F2 | 58 | -30 | 0 | 28 | -13 | 198 | 30 | -17 | -198
| 63 | 12 | Hurr 85 | 49 | 1 | S1 | 159 | -577 | 1 | 83 | -286 | 3213 | 76 | -291 | -3213
| 63 | 12 | Hurr 85 | 49 | 2 | S2 | 159 | -577 | 1 | 83 | -286 | 3213 | 76 | -291 | -3213
| 63 | 12 | Hurr 85 | 49 | 3 | S3 | 159 | -578 | 0 | 83 | -286 | 3213 | 76 | -292 | -3213
| 63 | 12 | Hurr 85 | 50 | 1 | S4 | 159 | -548 | 1 | 83 | -271 | 3215 | 75 | -278 | -3214
| 63 | 12 | Hurr 85 | 50 | 2 | S5 | 159 | -548 | 1 | 83 | -270 | 3215 | 75 | -277 | -3214
| 63 | 12 | Hurr 85 | 50 | 3 | S6 | 159 | -547 | 1 | 83 | -270 | 3215 | 75 | -277 | -3214
| 63 | 12 | Hurr 85 | 53 | 1 | S7 | 72 | -82 | 0 | 35 | -39 | 474 | 37 | -43 | -474
| 63 | 12 | Hurr 85 | 54 | 1 | S8 | 72 | -78 | 0 | 35 | -37 | 474 | 36 | -41 | -474
| 63 | 12 | Hurr 85 | 57 | 1 | PT:P1 | 54 | -51 | 1 | 26 | -22 | 329 | 28 | -29 | -329
| 63 | 12 | Hurr 85 | 58 | 1 | PT:P2 | 54 | -51 | 1 | 26 | -22 | 329 | 28 | -29 | -329
| 63 | 12 | Hurr 85 | 59 | 1 | PT:P3 | 54 | -51 | 1 | 26 | -22 | 329 | 28 | -29 | -329
| 63 | 12 | Hurr 85 | 60 | 1 | PT:P4 | 54 | -51 | 1 | 26 | -22 | 329 | 28 | -29 | -329
| 64 | 12 | Hurr 90 | 1 | 1 | TL-S1 | 259 | -740 | 0 | 140 | -372 | 3584 | 119 | -369 | -3584
| 64 | 12 | Hurr 90 | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 64 | 12 | Hurr 90 | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 64 | 12 | Hurr 90 | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 64 | 12 | Hurr 90 | 10 | 1 | ST1 | 759 | -1865 | 1 | 390 | -927 | 10708 | 370 | -938 | -10707
| 64 | 12 | Hurr 90 | 10 | 2 | ST2 | 759 | -1861 | 1 | 390 | -925 | 10708 | 370 | -936 | -10707
| 64 | 12 | Hurr 90 | 10 | 3 | ST3 | 759 | -1857 | 1 | 390 | -923 | 10708 | 370 | -934 | -10708
| 64 | 12 | Hurr 90 | 46 | 1 | F2 | 58 | -34 | 0 | 28 | -16 | 198 | 30 | -18 | -198
| 64 | 12 | Hurr 90 | 49 | 1 | S1 | 159 | -584 | 0 | 83 | -290 | 3213 | 76 | -293 | -3213
| 64 | 12 | Hurr 90 | 49 | 2 | S2 | 159 | -584 | 0 | 83 | -291 | 3213 | 76 | -293 | -3213
| 64 | 12 | Hurr 90 | 49 | 3 | S3 | 159 | -584 | 0 | 83 | -291 | 3213 | 76 | -293 | -3213
| 64 | 12 | Hurr 90 | 50 | 1 | S4 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 64 | 12 | Hurr 90 | 50 | 2 | S5 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 64 | 12 | Hurr 90 | 50 | 3 | S6 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 64 | 12 | Hurr 90 | 53 | 1 | S7 | 72 | -86 | 0 | 35 | -42 | 474 | 37 | -44 | -474
| 64 | 12 | Hurr 90 | 54 | 1 | S8 | 72 | -82 | 0 | 35 | -40 | 474 | 36 | -42 | -474
| 64 | 12 | Hurr 90 | 57 | 1 | PT:P1 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 64 | 12 | Hurr 90 | 58 | 1 | PT:P2 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 64 | 12 | Hurr 90 | 59 | 1 | PT:P3 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 64 | 12 | Hurr 90 | 60 | 1 | PT:P4 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 65 | 12 | Hurr -90M | 1 | 1 | TL-S1 | 259 | -740 | 0 | 140 | -372 | 3584 | 119 | -369 | -3584
| 65 | 12 | Hurr -90M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 65 | 12 | Hurr -90M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 65 | 12 | Hurr -90M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 65 | 12 | Hurr -90M | 10 | 1 | ST1 | 759 | -1865 | 1 | 390 | -927 | 10708 | 370 | -938 | -10707
| 65 | 12 | Hurr -90M | 10 | 2 | ST2 | 759 | -1861 | 1 | 390 | -925 | 10708 | 370 | -936 | -10707
| 65 | 12 | Hurr -90M | 10 | 3 | ST3 | 759 | -1857 | 1 | 390 | -923 | 10708 | 370 | -934 | -10708
| 65 | 12 | Hurr -90M | 46 | 1 | F2 | 58 | -34 | 0 | 28 | -16 | 198 | 30 | -18 | -198
| 65 | 12 | Hurr -90M | 49 | 1 | S1 | 159 | -584 | 0 | 83 | -290 | 3213 | 76 | -293 | -3213
| 65 | 12 | Hurr -90M | 49 | 2 | S2 | 159 | -584 | 0 | 83 | -291 | 3213 | 76 | -293 | -3213
| 65 | 12 | Hurr -90M | 49 | 3 | S3 | 159 | -584 | 0 | 83 | -291 | 3213 | 76 | -293 | -3213
| 65 | 12 | Hurr -90M | 50 | 1 | S4 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 65 | 12 | Hurr -90M | 50 | 2 | S5 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 65 | 12 | Hurr -90M | 50 | 3 | S6 | 159 | -554 | 0 | 83 | -275 | 3214 | 75 | -279 | -3214
| 65 | 12 | Hurr -90M | 53 | 1 | S7 | 72 | -86 | 0 | 35 | -42 | 474 | 37 | -44 | -474
| 65 | 12 | Hurr -90M | 54 | 1 | S8 | 72 | -82 | 0 | 35 | -40 | 474 | 36 | -42 | -474
| 65 | 12 | Hurr -90M | 57 | 1 | PT:P1 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 65 | 12 | Hurr -90M | 58 | 1 | PT:P2 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 65 | 12 | Hurr -90M | 59 | 1 | PT:P3 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 65 | 12 | Hurr -90M | 60 | 1 | PT:P4 | 54 | -58 | 0 | 26 | -27 | 329 | 28 | -31 | -328
| 66 | 12 | Hurr -85M | 1 | 1 | TL-S1 | 259 | -748 | 0 | 140 | -374 | 3584 | 119 | -374 | -3584
| 66 | 12 | Hurr -85M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 66 | 12 | Hurr -85M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 66 | 12 | Hurr -85M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 66 | 12 | Hurr -85M | 10 | 1 | ST1 | 759 | -1900 | 2 | 390 | -939 | 10708 | 370 | -960 | -10706
| 66 | 12 | Hurr -85M | 10 | 2 | ST2 | 759 | -1895 | 2 | 390 | -937 | 10708 | 370 | -958 | -10706
| 66 | 12 | Hurr -85M | 10 | 3 | ST3 | 759 | -1891 | 2 | 390 | -935 | 10708 | 370 | -956 | -10706
| 66 | 12 | Hurr -85M | 46 | 1 | F2 | 58 | -39 | 0 | 28 | -17 | 198 | 30 | -22 | -197
| 66 | 12 | Hurr -85M | 49 | 1 | S1 | 159 | -591 | 1 | 83 | -292 | 3213 | 76 | -299 | -3212
| 66 | 12 | Hurr -85M | 49 | 2 | S2 | 159 | -591 | 1 | 83 | -292 | 3213 | 76 | -299 | -3212
| 66 | 12 | Hurr -85M | 49 | 3 | S3 | 159 | -591 | 1 | 83 | -292 | 3213 | 76 | -299 | -3212
| 66 | 12 | Hurr -85M | 50 | 1 | S4 | 159 | -561 | 1 | 83 | -277 | 3214 | 75 | -285 | -3214
| 66 | 12 | Hurr -85M | 50 | 2 | S5 | 159 | -561 | 1 | 83 | -276 | 3214 | 75 | -284 | -3214
| 66 | 12 | Hurr -85M | 50 | 3 | S6 | 159 | -560 | 1 | 83 | -276 | 3214 | 75 | -284 | -3214
| 66 | 12 | Hurr -85M | 53 | 1 | S7 | 72 | -91 | 0 | 35 | -43 | 474 | 37 | -48 | -473
| 66 | 12 | Hurr -85M | 54 | 1 | S8 | 72 | -86 | 0 | 35 | -41 | 474 | 36 | -45 | -474
| 66 | 12 | Hurr -85M | 57 | 1 | PT:P1 | 54 | -67 | 1 | 26 | -29 | 329 | 28 | -38 | -328
| 66 | 12 | Hurr -85M | 58 | 1 | PT:P2 | 54 | -67 | 1 | 26 | -29 | 329 | 28 | -38 | -328
| 66 | 12 | Hurr -85M | 59 | 1 | PT:P3 | 54 | -67 | 1 | 26 | -29 | 329 | 28 | -38 | -328
| 66 | 12 | Hurr -85M | 60 | 1 | PT:P4 | 54 | -67 | 1 | 26 | -29 | 329 | 28 | -38 | -328
| 67 | 12 | Hurr -80M | 1 | 1 | TL-S1 | 259 | -757 | 1 | 140 | -376 | 3584 | 119 | -382 | -3583
| 67 | 12 | Hurr -80M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 67 | 12 | Hurr -80M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 67 | 12 | Hurr -80M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 67 | 12 | Hurr -80M | 10 | 1 | ST1 | 759 | -1943 | 3 | 390 | -952 | 10707 | 370 | -991 | -10704
| 67 | 12 | Hurr -80M | 10 | 2 | ST2 | 759 | -1939 | 3 | 390 | -950 | 10708 | 370 | -989 | -10704
| 67 | 12 | Hurr -80M | 10 | 3 | ST3 | 759 | -1934 | 3 | 390 | -948 | 10708 | 370 | -986 | -10704
| 67 | 12 | Hurr -80M | 46 | 1 | F2 | 58 | -47 | 1 | 28 | -19 | 203 | 30 | -29 | -202
| 67 | 12 | Hurr -80M | 49 | 1 | S1 | 159 | -601 | 1 | 83 | -294 | 3213 | 76 | -307 | -3211
| 67 | 12 | Hurr -80M | 49 | 2 | S2 | 159 | -601 | 1 | 83 | -294 | 3213 | 76 | -307 | -3211
| 67 | 12 | Hurr -80M | 49 | 3 | S3 | 159 | -601 | 1 | 83 | -294 | 3213 | 76 | -307 | -3211
| 67 | 12 | Hurr -80M | 50 | 1 | S4 | 159 | -571 | 1 | 83 | -278 | 3214 | 75 | -293 | -3213
| 67 | 12 | Hurr -80M | 50 | 2 | S5 | 159 | -571 | 1 | 83 | -278 | 3214 | 75 | -293 | -3213
| 67 | 12 | Hurr -80M | 50 | 3 | S6 | 159 | -570 | 1 | 83 | -278 | 3214 | 75 | -292 | -3213
| 67 | 12 | Hurr -80M | 53 | 1 | S7 | 72 | -98 | 1 | 35 | -44 | 477 | 37 | -53 | -477
| 67 | 12 | Hurr -80M | 54 | 1 | S8 | 72 | -92 | 1 | 35 | -42 | 478 | 36 | -51 | -477
| 67 | 12 | Hurr -80M | 57 | 1 | PT:P1 | 54 | -81 | 2 | 26 | -32 | 341 | 28 | -49 | -339
| 67 | 12 | Hurr -80M | 58 | 1 | PT:P2 | 54 | -81 | 2 | 26 | -32 | 341 | 28 | -49 | -339
| 67 | 12 | Hurr -80M | 59 | 1 | PT:P3 | 54 | -81 | 2 | 26 | -32 | 341 | 28 | -49 | -339
| 67 | 12 | Hurr -80M | 60 | 1 | PT:P4 | 54 | -81 | 2 | 26 | -32 | 341 | 28 | -49 | -339
| 68 | 12 | Hurr -75M | 1 | 1 | TL-S1 | 259 | -772 | 1 | 141 | -380 | 3587 | 119 | -392 | -3586
| 68 | 12 | Hurr -75M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 68 | 12 | Hurr -75M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 68 | 12 | Hurr -75M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 68 | 12 | Hurr -75M | 10 | 1 | ST1 | 760 | -2007 | 5 | 390 | -975 | 10728 | 370 | -1033 | -10722
| 68 | 12 | Hurr -75M | 10 | 2 | ST2 | 760 | -2002 | 5 | 390 | -972 | 10728 | 370 | -1030 | -10723
| 68 | 12 | Hurr -75M | 10 | 3 | ST3 | 760 | -1996 | 5 | 390 | -970 | 10728 | 370 | -1026 | -10723
| 68 | 12 | Hurr -75M | 46 | 1 | F2 | 58 | -63 | 1 | 28 | -24 | 224 | 30 | -39 | -223
| 68 | 12 | Hurr -75M | 49 | 1 | S1 | 159 | -619 | 2 | 83 | -299 | 3223 | 76 | -320 | -3221
| 68 | 12 | Hurr -75M | 49 | 2 | S2 | 159 | -619 | 2 | 83 | -299 | 3223 | 76 | -320 | -3221
| 68 | 12 | Hurr -75M | 49 | 3 | S3 | 159 | -619 | 2 | 83 | -299 | 3223 | 76 | -320 | -3221
| 68 | 12 | Hurr -75M | 50 | 1 | S4 | 159 | -590 | 2 | 83 | -284 | 3225 | 75 | -306 | -3223
| 68 | 12 | Hurr -75M | 50 | 2 | S5 | 159 | -589 | 2 | 83 | -284 | 3225 | 75 | -305 | -3223
| 68 | 12 | Hurr -75M | 50 | 3 | S6 | 159 | -588 | 2 | 83 | -283 | 3225 | 75 | -305 | -3223
| 68 | 12 | Hurr -75M | 53 | 1 | S7 | 72 | -110 | 1 | 36 | -49 | 493 | 37 | -62 | -491
| 68 | 12 | Hurr -75M | 54 | 1 | S8 | 72 | -105 | 1 | 36 | -46 | 493 | 37 | -59 | -492
| 68 | 12 | Hurr -75M | 57 | 1 | PT:P1 | 54 | -109 | 2 | 26 | -42 | 386 | 28 | -67 | -384
| 68 | 12 | Hurr -75M | 58 | 1 | PT:P2 | 54 | -109 | 2 | 26 | -42 | 386 | 28 | -67 | -384
| 68 | 12 | Hurr -75M | 59 | 1 | PT:P3 | 54 | -109 | 2 | 26 | -42 | 386 | 28 | -67 | -384
| 68 | 12 | Hurr -75M | 60 | 1 | PT:P4 | 54 | -109 | 2 | 26 | -42 | 386 | 28 | -67 | -384
| 69 | 12 | Hurr -70M | 1 | 1 | TL-S1 | 260 | -793 | 2 | 141 | -387 | 3600 | 119 | -406 | -3598
| 69 | 12 | Hurr -70M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 69 | 12 | Hurr -70M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 69 | 12 | Hurr -70M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 69 | 12 | Hurr -70M | 10 | 1 | ST1 | 760 | -2090 | 7 | 390 | -1007 | 10768 | 370 | -1083 | -10762
| 69 | 12 | Hurr -70M | 10 | 2 | ST2 | 760 | -2083 | 7 | 390 | -1004 | 10768 | 370 | -1079 | -10762
| 69 | 12 | Hurr -70M | 10 | 3 | ST3 | 760 | -2077 | 6 | 390 | -1001 | 10769 | 370 | -1075 | -10762
| 69 | 12 | Hurr -70M | 46 | 1 | F2 | 59 | -87 | 2 | 29 | -33 | 270 | 30 | -53 | -268
| 69 | 12 | Hurr -70M | 49 | 1 | S1 | 159 | -646 | 3 | 83 | -309 | 3250 | 76 | -337 | -3247
| 69 | 12 | Hurr -70M | 49 | 2 | S2 | 159 | -646 | 3 | 83 | -309 | 3250 | 76 | -337 | -3247
| 69 | 12 | Hurr -70M | 49 | 3 | S3 | 159 | -646 | 2 | 83 | -309 | 3250 | 76 | -337 | -3247
| 69 | 12 | Hurr -70M | 50 | 1 | S4 | 159 | -616 | 2 | 83 | -294 | 3251 | 75 | -322 | -3249
| 69 | 12 | Hurr -70M | 50 | 2 | S5 | 159 | -616 | 2 | 83 | -294 | 3251 | 75 | -322 | -3249
| 69 | 12 | Hurr -70M | 50 | 3 | S6 | 159 | -615 | 2 | 83 | -293 | 3251 | 75 | -321 | -3249
| 69 | 12 | Hurr -70M | 53 | 1 | S7 | 72 | -130 | 2 | 36 | -57 | 529 | 37 | -74 | -527
| 69 | 12 | Hurr -70M | 54 | 1 | S8 | 72 | -125 | 1 | 36 | -54 | 529 | 37 | -71 | -528
| 69 | 12 | Hurr -70M | 57 | 1 | PT:P1 | 55 | -152 | 3 | 27 | -59 | 480 | 28 | -93 | -477
| 69 | 12 | Hurr -70M | 58 | 1 | PT:P2 | 55 | -152 | 3 | 27 | -59 | 479 | 28 | -93 | -476
| 69 | 12 | Hurr -70M | 59 | 1 | PT:P3 | 55 | -152 | 3 | 27 | -59 | 479 | 28 | -93 | -476
| 69 | 12 | Hurr -70M | 60 | 1 | PT:P4 | 55 | -151 | 3 | 27 | -59 | 479 | 28 | -93 | -476
| 70 | 12 | Hurr -65M | 1 | 1 | TL-S1 | 261 | -820 | 3 | 141 | -398 | 3621 | 120 | -422 | -3618
| 70 | 12 | Hurr -65M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 70 | 12 | Hurr -65M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 70 | 12 | Hurr -65M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 70 | 12 | Hurr -65M | 10 | 1 | ST1 | 762 | -2196 | 8 | 391 | -1051 | 10872 | 370 | -1145 | -10863
| 70 | 12 | Hurr -65M | 10 | 2 | ST2 | 761 | -2189 | 8 | 391 | -1048 | 10872 | 370 | -1140 | -10864
| 70 | 12 | Hurr -65M | 10 | 3 | ST3 | 761 | -2181 | 8 | 391 | -1045 | 10872 | 370 | -1135 | -10864
| 70 | 12 | Hurr -65M | 46 | 1 | F2 | 59 | -118 | 2 | 29 | -47 | 338 | 30 | -71 | -336
| 70 | 12 | Hurr -65M | 49 | 1 | S1 | 159 | -682 | 3 | 84 | -324 | 3298 | 76 | -358 | -3295
| 70 | 12 | Hurr -65M | 49 | 2 | S2 | 159 | -682 | 3 | 84 | -324 | 3298 | 76 | -358 | -3295
| 70 | 12 | Hurr -65M | 49 | 3 | S3 | 159 | -682 | 3 | 84 | -324 | 3298 | 76 | -358 | -3295
| 70 | 12 | Hurr -65M | 50 | 1 | S4 | 159 | -652 | 3 | 84 | -309 | 3299 | 75 | -343 | -3296
| 70 | 12 | Hurr -65M | 50 | 2 | S5 | 159 | -651 | 3 | 84 | -308 | 3299 | 75 | -343 | -3296
| 70 | 12 | Hurr -65M | 50 | 3 | S6 | 159 | -650 | 3 | 84 | -308 | 3299 | 75 | -342 | -3296
| 70 | 12 | Hurr -65M | 53 | 1 | S7 | 73 | -158 | 2 | 36 | -68 | 591 | 37 | -90 | -589
| 70 | 12 | Hurr -65M | 54 | 1 | S8 | 73 | -152 | 2 | 36 | -66 | 591 | 37 | -86 | -590
| 70 | 12 | Hurr -65M | 57 | 1 | PT:P1 | 56 | -208 | 4 | 28 | -83 | 614 | 28 | -125 | -611
| 70 | 12 | Hurr -65M | 58 | 1 | PT:P2 | 56 | -208 | 4 | 28 | -83 | 614 | 28 | -125 | -610
| 70 | 12 | Hurr -65M | 59 | 1 | PT:P3 | 56 | -208 | 4 | 28 | -83 | 613 | 28 | -125 | -610
| 70 | 12 | Hurr -65M | 60 | 1 | PT:P4 | 56 | -208 | 4 | 28 | -83 | 612 | 28 | -124 | -609
| 71 | 12 | Hurr -60M | 1 | 1 | TL-S1 | 263 | -854 | 3 | 143 | -412 | 3663 | 120 | -442 | -3660
| 71 | 12 | Hurr -60M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 71 | 12 | Hurr -60M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 71 | 12 | Hurr -60M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 71 | 12 | Hurr -60M | 10 | 1 | ST1 | 764 | -2326 | 9 | 393 | -1109 | 11048 | 371 | -1217 | -11038
| 71 | 12 | Hurr -60M | 10 | 2 | ST2 | 764 | -2317 | 9 | 393 | -1105 | 11048 | 371 | -1212 | -11039
| 71 | 12 | Hurr -60M | 10 | 3 | ST3 | 764 | -2307 | 9 | 393 | -1101 | 11048 | 371 | -1206 | -11039
| 71 | 12 | Hurr -60M | 46 | 1 | F2 | 59 | -155 | 2 | 30 | -63 | 423 | 30 | -92 | -421
| 71 | 12 | Hurr -60M | 49 | 1 | S1 | 160 | -727 | 4 | 84 | -343 | 3372 | 76 | -384 | -3369
| 71 | 12 | Hurr -60M | 49 | 2 | S2 | 160 | -727 | 4 | 84 | -343 | 3372 | 76 | -383 | -3369
| 71 | 12 | Hurr -60M | 49 | 3 | S3 | 160 | -726 | 4 | 84 | -343 | 3372 | 76 | -383 | -3369
| 71 | 12 | Hurr -60M | 50 | 1 | S4 | 159 | -696 | 3 | 84 | -328 | 3374 | 75 | -368 | -3370
| 71 | 12 | Hurr -60M | 50 | 2 | S5 | 159 | -695 | 3 | 84 | -327 | 3374 | 75 | -367 | -3371
| 71 | 12 | Hurr -60M | 50 | 3 | S6 | 159 | -693 | 3 | 84 | -327 | 3374 | 75 | -367 | -3371
| 71 | 12 | Hurr -60M | 53 | 1 | S7 | 73 | -193 | 2 | 37 | -84 | 677 | 37 | -109 | -675
| 71 | 12 | Hurr -60M | 54 | 1 | S8 | 73 | -186 | 2 | 37 | -81 | 677 | 37 | -105 | -675
| 71 | 12 | Hurr -60M | 57 | 1 | PT:P1 | 57 | -275 | 4 | 29 | -113 | 776 | 28 | -161 | -772
| 71 | 12 | Hurr -60M | 58 | 1 | PT:P2 | 57 | -274 | 4 | 29 | -113 | 775 | 28 | -161 | -771
| 71 | 12 | Hurr -60M | 59 | 1 | PT:P3 | 57 | -274 | 4 | 29 | -113 | 775 | 28 | -161 | -770
| 71 | 12 | Hurr -60M | 60 | 1 | PT:P4 | 57 | -274 | 4 | 29 | -113 | 774 | 28 | -161 | -770
| 72 | 12 | Hurr -55M | 1 | 1 | TL-S1 | 265 | -893 | 3 | 144 | -430 | 3713 | 121 | -463 | -3710
| 72 | 12 | Hurr -55M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 72 | 12 | Hurr -55M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 72 | 12 | Hurr -55M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 72 | 12 | Hurr -55M | 10 | 1 | ST1 | 767 | -2474 | 11 | 395 | -1176 | 11285 | 372 | -1298 | -11275
| 72 | 12 | Hurr -55M | 10 | 2 | ST2 | 767 | -2464 | 10 | 395 | -1172 | 11286 | 372 | -1292 | -11275
| 72 | 12 | Hurr -55M | 10 | 3 | ST3 | 767 | -2453 | 10 | 395 | -1167 | 11286 | 372 | -1285 | -11276
| 72 | 12 | Hurr -55M | 46 | 1 | F2 | 60 | -197 | 3 | 30 | -82 | 517 | 30 | -114 | -515
| 72 | 12 | Hurr -55M | 49 | 1 | S1 | 160 | -781 | 4 | 85 | -368 | 3478 | 76 | -413 | -3474
| 72 | 12 | Hurr -55M | 49 | 2 | S2 | 160 | -780 | 4 | 85 | -368 | 3479 | 76 | -413 | -3474
| 72 | 12 | Hurr -55M | 49 | 3 | S3 | 160 | -779 | 4 | 85 | -367 | 3479 | 76 | -412 | -3475
| 72 | 12 | Hurr -55M | 50 | 1 | S4 | 160 | -749 | 4 | 84 | -352 | 3480 | 75 | -397 | -3476
| 72 | 12 | Hurr -55M | 50 | 2 | S5 | 160 | -747 | 4 | 84 | -351 | 3480 | 75 | -396 | -3476
| 72 | 12 | Hurr -55M | 50 | 3 | S6 | 160 | -746 | 4 | 84 | -351 | 3480 | 75 | -395 | -3476
| 72 | 12 | Hurr -55M | 53 | 1 | S7 | 74 | -232 | 3 | 37 | -102 | 779 | 37 | -130 | -776
| 72 | 12 | Hurr -55M | 54 | 1 | S8 | 74 | -224 | 2 | 37 | -99 | 780 | 37 | -126 | -777
| 72 | 12 | Hurr -55M | 57 | 1 | PT:P1 | 58 | -347 | 5 | 30 | -147 | 953 | 28 | -201 | -949
| 72 | 12 | Hurr -55M | 58 | 1 | PT:P2 | 58 | -347 | 5 | 30 | -146 | 952 | 28 | -201 | -948
| 72 | 12 | Hurr -55M | 59 | 1 | PT:P3 | 58 | -347 | 5 | 30 | -146 | 951 | 28 | -200 | -946
| 72 | 12 | Hurr -55M | 60 | 1 | PT:P4 | 58 | -346 | 5 | 30 | -146 | 950 | 28 | -200 | -945
| 73 | 12 | Hurr -50M | 1 | 1 | TL-S1 | 269 | -938 | 3 | 146 | -451 | 3785 | 123 | -487 | -3782
| 73 | 12 | Hurr -50M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 73 | 12 | Hurr -50M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 73 | 12 | Hurr -50M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 73 | 12 | Hurr -50M | 10 | 1 | ST1 | 770 | -2640 | 11 | 398 | -1254 | 11593 | 373 | -1386 | -11581
| 73 | 12 | Hurr -50M | 10 | 2 | ST2 | 770 | -2628 | 11 | 398 | -1249 | 11593 | 373 | -1379 | -11582
| 73 | 12 | Hurr -50M | 10 | 3 | ST3 | 770 | -2615 | 11 | 398 | -1243 | 11594 | 373 | -1371 | -11583
| 73 | 12 | Hurr -50M | 46 | 1 | F2 | 61 | -240 | 3 | 31 | -103 | 616 | 30 | -138 | -613
| 73 | 12 | Hurr -50M | 49 | 1 | S1 | 161 | -841 | 4 | 85 | -396 | 3605 | 76 | -445 | -3600
| 73 | 12 | Hurr -50M | 49 | 2 | S2 | 161 | -840 | 4 | 85 | -396 | 3605 | 76 | -444 | -3600
| 73 | 12 | Hurr -50M | 49 | 3 | S3 | 161 | -839 | 4 | 85 | -395 | 3605 | 76 | -444 | -3600
| 73 | 12 | Hurr -50M | 50 | 1 | S4 | 160 | -808 | 4 | 85 | -379 | 3607 | 75 | -428 | -3602
| 73 | 12 | Hurr -50M | 50 | 2 | S5 | 160 | -806 | 4 | 85 | -379 | 3607 | 75 | -427 | -3602
| 73 | 12 | Hurr -50M | 50 | 3 | S6 | 160 | -804 | 4 | 85 | -378 | 3607 | 75 | -426 | -3603
| 73 | 12 | Hurr -50M | 53 | 1 | S7 | 75 | -275 | 3 | 38 | -122 | 890 | 37 | -153 | -887
| 73 | 12 | Hurr -50M | 54 | 1 | S8 | 74 | -266 | 3 | 38 | -118 | 891 | 37 | -148 | -889
| 73 | 12 | Hurr -50M | 57 | 1 | PT:P1 | 59 | -424 | 5 | 31 | -182 | 1136 | 28 | -242 | -1130
| 73 | 12 | Hurr -50M | 58 | 1 | PT:P2 | 59 | -423 | 5 | 31 | -182 | 1135 | 28 | -241 | -1129
| 73 | 12 | Hurr -50M | 59 | 1 | PT:P3 | 59 | -423 | 5 | 31 | -182 | 1133 | 28 | -241 | -1128
| 73 | 12 | Hurr -50M | 60 | 1 | PT:P4 | 59 | -422 | 5 | 31 | -182 | 1132 | 28 | -241 | -1127
| 74 | 12 | Hurr -45M | 1 | 1 | TL-S1 | 272 | -985 | 3 | 148 | -473 | 3865 | 124 | -512 | -3862
| 74 | 12 | Hurr -45M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 74 | 12 | Hurr -45M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 74 | 12 | Hurr -45M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 74 | 12 | Hurr -45M | 10 | 1 | ST1 | 774 | -2815 | 12 | 401 | -1337 | 11938 | 374 | -1477 | -11926
| 74 | 12 | Hurr -45M | 10 | 2 | ST2 | 774 | -2801 | 12 | 401 | -1331 | 11939 | 374 | -1469 | -11927
| 74 | 12 | Hurr -45M | 10 | 3 | ST3 | 774 | -2786 | 12 | 401 | -1325 | 11939 | 374 | -1461 | -11928
| 74 | 12 | Hurr -45M | 46 | 1 | F2 | 61 | -285 | 3 | 31 | -124 | 714 | 30 | -161 | -711
| 74 | 12 | Hurr -45M | 49 | 1 | S1 | 161 | -905 | 5 | 86 | -426 | 3745 | 75 | -478 | -3741
| 74 | 12 | Hurr -45M | 49 | 2 | S2 | 161 | -903 | 5 | 86 | -426 | 3745 | 75 | -478 | -3741
| 74 | 12 | Hurr -45M | 49 | 3 | S3 | 161 | -902 | 5 | 86 | -425 | 3745 | 75 | -477 | -3741
| 74 | 12 | Hurr -45M | 50 | 1 | S4 | 161 | -870 | 4 | 86 | -409 | 3747 | 75 | -461 | -3743
| 74 | 12 | Hurr -45M | 50 | 2 | S5 | 161 | -868 | 4 | 86 | -408 | 3747 | 75 | -460 | -3743
| 74 | 12 | Hurr -45M | 50 | 3 | S6 | 161 | -865 | 4 | 86 | -407 | 3747 | 75 | -458 | -3743
| 74 | 12 | Hurr -45M | 53 | 1 | S7 | 75 | -319 | 3 | 38 | -144 | 1005 | 37 | -175 | -1002
| 74 | 12 | Hurr -45M | 54 | 1 | S8 | 75 | -309 | 3 | 38 | -139 | 1006 | 37 | -170 | -1003
| 74 | 12 | Hurr -45M | 57 | 1 | PT:P1 | 60 | -502 | 6 | 32 | -220 | 1317 | 28 | -282 | -1312
| 74 | 12 | Hurr -45M | 58 | 1 | PT:P2 | 60 | -501 | 6 | 32 | -219 | 1316 | 28 | -282 | -1310
| 74 | 12 | Hurr -45M | 59 | 1 | PT:P3 | 60 | -500 | 5 | 32 | -219 | 1314 | 28 | -281 | -1309
| 74 | 12 | Hurr -45M | 60 | 1 | PT:P4 | 60 | -500 | 5 | 32 | -219 | 1313 | 28 | -281 | -1307
| 75 | 12 | Hurr -40M | 1 | 1 | TL-S1 | 277 | -1035 | 3 | 151 | -498 | 3959 | 126 | -538 | -3956
| 75 | 12 | Hurr -40M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 75 | 12 | Hurr -40M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 75 | 12 | Hurr -40M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 75 | 12 | Hurr -40M | 10 | 1 | ST1 | 779 | -2993 | 12 | 404 | -1424 | 12310 | 375 | -1569 | -12298
| 75 | 12 | Hurr -40M | 10 | 2 | ST2 | 779 | -2977 | 12 | 404 | -1417 | 12311 | 375 | -1560 | -12298
| 75 | 12 | Hurr -40M | 10 | 3 | ST3 | 779 | -2960 | 12 | 404 | -1410 | 12311 | 375 | -1550 | -12299
| 75 | 12 | Hurr -40M | 46 | 1 | F2 | 62 | -328 | 3 | 32 | -145 | 809 | 30 | -183 | -806
| 75 | 12 | Hurr -40M | 49 | 1 | S1 | 162 | -970 | 5 | 86 | -458 | 3895 | 75 | -512 | -3890
| 75 | 12 | Hurr -40M | 49 | 2 | S2 | 162 | -968 | 5 | 86 | -457 | 3895 | 75 | -511 | -3890
| 75 | 12 | Hurr -40M | 49 | 3 | S3 | 162 | -966 | 5 | 86 | -457 | 3895 | 75 | -510 | -3890
| 75 | 12 | Hurr -40M | 50 | 1 | S4 | 161 | -934 | 5 | 86 | -440 | 3897 | 75 | -494 | -3892
| 75 | 12 | Hurr -40M | 50 | 2 | S5 | 161 | -931 | 5 | 86 | -439 | 3897 | 75 | -492 | -3892
| 75 | 12 | Hurr -40M | 50 | 3 | S6 | 161 | -928 | 5 | 86 | -438 | 3897 | 75 | -491 | -3892
| 75 | 12 | Hurr -40M | 53 | 1 | S7 | 76 | -363 | 3 | 39 | -165 | 1118 | 37 | -198 | -1115
| 75 | 12 | Hurr -40M | 54 | 1 | S8 | 76 | -351 | 3 | 39 | -159 | 1119 | 37 | -192 | -1116
| 75 | 12 | Hurr -40M | 57 | 1 | PT:P1 | 61 | -578 | 6 | 33 | -257 | 1493 | 28 | -321 | -1487
| 75 | 12 | Hurr -40M | 58 | 1 | PT:P2 | 61 | -577 | 6 | 33 | -256 | 1491 | 28 | -321 | -1485
| 75 | 12 | Hurr -40M | 59 | 1 | PT:P3 | 61 | -577 | 6 | 33 | -256 | 1489 | 28 | -321 | -1484
| 75 | 12 | Hurr -40M | 60 | 1 | PT:P4 | 61 | -576 | 6 | 33 | -256 | 1488 | 28 | -320 | -1482
| 76 | 12 | Hurr -35M | 1 | 1 | TL-S1 | 281 | -1085 | 3 | 153 | -522 | 4052 | 128 | -562 | -4049
| 76 | 12 | Hurr -35M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 76 | 12 | Hurr -35M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 76 | 12 | Hurr -35M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 76 | 12 | Hurr -35M | 10 | 1 | ST1 | 784 | -3169 | 13 | 408 | -1511 | 12697 | 376 | -1657 | -12685
| 76 | 12 | Hurr -35M | 10 | 2 | ST2 | 784 | -3151 | 12 | 408 | -1504 | 12698 | 376 | -1648 | -12686
| 76 | 12 | Hurr -35M | 10 | 3 | ST3 | 784 | -3132 | 12 | 408 | -1496 | 12699 | 376 | -1637 | -12687
| 76 | 12 | Hurr -35M | 46 | 1 | F2 | 62 | -370 | 3 | 32 | -166 | 899 | 30 | -205 | -895
| 76 | 12 | Hurr -35M | 49 | 1 | S1 | 162 | -1033 | 5 | 87 | -490 | 4042 | 75 | -544 | -4037
| 76 | 12 | Hurr -35M | 49 | 2 | S2 | 162 | -1031 | 5 | 87 | -489 | 4042 | 75 | -543 | -4037
| 76 | 12 | Hurr -35M | 49 | 3 | S3 | 162 | -1029 | 5 | 87 | -488 | 4042 | 75 | -541 | -4037
| 76 | 12 | Hurr -35M | 50 | 1 | S4 | 162 | -996 | 5 | 87 | -471 | 4044 | 75 | -525 | -4040
| 76 | 12 | Hurr -35M | 50 | 2 | S5 | 162 | -993 | 5 | 87 | -469 | 4044 | 75 | -523 | -4040
| 76 | 12 | Hurr -35M | 50 | 3 | S6 | 162 | -990 | 5 | 87 | -468 | 4044 | 75 | -522 | -4040
| 76 | 12 | Hurr -35M | 53 | 1 | S7 | 77 | -404 | 3 | 40 | -186 | 1225 | 37 | -219 | -1222
| 76 | 12 | Hurr -35M | 54 | 1 | S8 | 77 | -392 | 3 | 40 | -180 | 1226 | 37 | -212 | -1224
| 76 | 12 | Hurr -35M | 57 | 1 | PT:P1 | 62 | -651 | 6 | 34 | -293 | 1657 | 29 | -358 | -1651
| 76 | 12 | Hurr -35M | 58 | 1 | PT:P2 | 62 | -650 | 6 | 34 | -293 | 1655 | 28 | -358 | -1649
| 76 | 12 | Hurr -35M | 59 | 1 | PT:P3 | 62 | -650 | 6 | 34 | -292 | 1653 | 28 | -357 | -1647
| 76 | 12 | Hurr -35M | 60 | 1 | PT:P4 | 62 | -649 | 6 | 34 | -292 | 1651 | 28 | -357 | -1646
| 77 | 12 | Hurr -30M | 1 | 1 | TL-S1 | 285 | -1132 | 3 | 156 | -546 | 4146 | 130 | -585 | -4143
| 77 | 12 | Hurr -30M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 77 | 12 | Hurr -30M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 77 | 12 | Hurr -30M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 77 | 12 | Hurr -30M | 10 | 1 | ST1 | 788 | -3335 | 12 | 411 | -1595 | 13071 | 377 | -1740 | -13058
| 77 | 12 | Hurr -30M | 10 | 2 | ST2 | 788 | -3316 | 12 | 411 | -1587 | 13071 | 377 | -1729 | -13059
| 77 | 12 | Hurr -30M | 10 | 3 | ST3 | 788 | -3295 | 12 | 411 | -1578 | 13072 | 377 | -1717 | -13060
| 77 | 12 | Hurr -30M | 46 | 1 | F2 | 63 | -409 | 3 | 33 | -185 | 980 | 30 | -224 | -976
| 77 | 12 | Hurr -30M | 49 | 1 | S1 | 163 | -1093 | 5 | 88 | -520 | 4183 | 75 | -573 | -4178
| 77 | 12 | Hurr -30M | 49 | 2 | S2 | 163 | -1091 | 5 | 88 | -519 | 4183 | 75 | -572 | -4178
| 77 | 12 | Hurr -30M | 49 | 3 | S3 | 163 | -1089 | 5 | 88 | -518 | 4183 | 75 | -571 | -4178
| 77 | 12 | Hurr -30M | 50 | 1 | S4 | 163 | -1055 | 5 | 88 | -500 | 4185 | 75 | -554 | -4180
| 77 | 12 | Hurr -30M | 50 | 2 | S5 | 163 | -1051 | 5 | 88 | -499 | 4185 | 75 | -552 | -4180
| 77 | 12 | Hurr -30M | 50 | 3 | S6 | 163 | -1048 | 5 | 88 | -498 | 4185 | 75 | -550 | -4181
| 77 | 12 | Hurr -30M | 53 | 1 | S7 | 77 | -443 | 3 | 40 | -205 | 1324 | 37 | -238 | -1321
| 77 | 12 | Hurr -30M | 54 | 1 | S8 | 77 | -430 | 3 | 40 | -199 | 1325 | 37 | -231 | -1323
| 77 | 12 | Hurr -30M | 57 | 1 | PT:P1 | 63 | -719 | 6 | 35 | -327 | 1806 | 29 | -392 | -1800
| 77 | 12 | Hurr -30M | 58 | 1 | PT:P2 | 63 | -718 | 6 | 35 | -327 | 1804 | 29 | -391 | -1799
| 77 | 12 | Hurr -30M | 59 | 1 | PT:P3 | 63 | -717 | 6 | 35 | -326 | 1802 | 29 | -391 | -1797
| 77 | 12 | Hurr -30M | 60 | 1 | PT:P4 | 63 | -716 | 6 | 35 | -326 | 1800 | 29 | -390 | -1795
| 78 | 12 | Hurr -25M | 1 | 1 | TL-S1 | 289 | -1174 | 3 | 158 | -569 | 4231 | 131 | -605 | -4228
| 78 | 12 | Hurr -25M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 78 | 12 | Hurr -25M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 78 | 12 | Hurr -25M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 78 | 12 | Hurr -25M | 10 | 1 | ST1 | 792 | -3485 | 12 | 414 | -1673 | 13410 | 378 | -1812 | -13398
| 78 | 12 | Hurr -25M | 10 | 2 | ST2 | 792 | -3464 | 12 | 414 | -1664 | 13411 | 378 | -1801 | -13399
| 78 | 12 | Hurr -25M | 10 | 3 | ST3 | 792 | -3442 | 11 | 414 | -1654 | 13412 | 378 | -1788 | -13401
| 78 | 12 | Hurr -25M | 46 | 1 | F2 | 63 | -444 | 3 | 33 | -203 | 1051 | 30 | -240 | -1048
| 78 | 12 | Hurr -25M | 49 | 1 | S1 | 163 | -1147 | 5 | 88 | -548 | 4309 | 75 | -599 | -4305
| 78 | 12 | Hurr -25M | 49 | 2 | S2 | 163 | -1145 | 5 | 88 | -547 | 4309 | 75 | -598 | -4305
| 78 | 12 | Hurr -25M | 49 | 3 | S3 | 163 | -1142 | 4 | 88 | -546 | 4309 | 75 | -596 | -4305
| 78 | 12 | Hurr -25M | 50 | 1 | S4 | 163 | -1107 | 4 | 88 | -528 | 4312 | 75 | -580 | -4307
| 78 | 12 | Hurr -25M | 50 | 2 | S5 | 163 | -1104 | 4 | 88 | -526 | 4312 | 75 | -578 | -4307
| 78 | 12 | Hurr -25M | 50 | 3 | S6 | 163 | -1100 | 4 | 88 | -525 | 4312 | 75 | -576 | -4308
| 78 | 12 | Hurr -25M | 53 | 1 | S7 | 78 | -478 | 3 | 41 | -223 | 1411 | 37 | -255 | -1408
| 78 | 12 | Hurr -25M | 54 | 1 | S8 | 78 | -464 | 3 | 41 | -216 | 1412 | 37 | -247 | -1410
| 78 | 12 | Hurr -25M | 57 | 1 | PT:P1 | 64 | -779 | 5 | 35 | -359 | 1938 | 29 | -421 | -1933
| 78 | 12 | Hurr -25M | 58 | 1 | PT:P2 | 64 | -778 | 5 | 35 | -358 | 1936 | 29 | -420 | -1930
| 78 | 12 | Hurr -25M | 59 | 1 | PT:P3 | 64 | -777 | 5 | 35 | -358 | 1933 | 29 | -420 | -1928
| 78 | 12 | Hurr -25M | 60 | 1 | PT:P4 | 64 | -776 | 5 | 35 | -357 | 1931 | 29 | -419 | -1926
| 79 | 12 | Hurr -20M | 1 | 1 | TL-S1 | 292 | -1212 | 2 | 160 | -589 | 4307 | 133 | -622 | -4305
| 79 | 12 | Hurr -20M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 79 | 12 | Hurr -20M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 79 | 12 | Hurr -20M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 79 | 12 | Hurr -20M | 10 | 1 | ST1 | 796 | -3615 | 11 | 417 | -1742 | 13708 | 379 | -1873 | -13697
| 79 | 12 | Hurr -20M | 10 | 2 | ST2 | 796 | -3593 | 11 | 417 | -1732 | 13709 | 379 | -1861 | -13698
| 79 | 12 | Hurr -20M | 10 | 3 | ST3 | 796 | -3570 | 11 | 417 | -1721 | 13710 | 379 | -1848 | -13699
| 79 | 12 | Hurr -20M | 46 | 1 | F2 | 64 | -473 | 3 | 34 | -219 | 1112 | 30 | -254 | -1109
| 79 | 12 | Hurr -20M | 49 | 1 | S1 | 164 | -1194 | 4 | 89 | -573 | 4420 | 75 | -621 | -4415
| 79 | 12 | Hurr -20M | 49 | 2 | S2 | 164 | -1192 | 4 | 89 | -572 | 4420 | 75 | -620 | -4415
| 79 | 12 | Hurr -20M | 49 | 3 | S3 | 164 | -1189 | 4 | 89 | -571 | 4420 | 75 | -618 | -4416
| 79 | 12 | Hurr -20M | 50 | 1 | S4 | 163 | -1153 | 4 | 89 | -552 | 4422 | 75 | -601 | -4418
| 79 | 12 | Hurr -20M | 50 | 2 | S5 | 163 | -1149 | 4 | 89 | -550 | 4422 | 75 | -599 | -4418
| 79 | 12 | Hurr -20M | 50 | 3 | S6 | 163 | -1146 | 4 | 89 | -549 | 4423 | 75 | -597 | -4418
| 79 | 12 | Hurr -20M | 53 | 1 | S7 | 78 | -508 | 3 | 41 | -239 | 1485 | 37 | -268 | -1483
| 79 | 12 | Hurr -20M | 54 | 1 | S8 | 78 | -493 | 3 | 41 | -232 | 1487 | 37 | -261 | -1484
| 79 | 12 | Hurr -20M | 57 | 1 | PT:P1 | 65 | -831 | 5 | 36 | -386 | 2049 | 29 | -445 | -2044
| 79 | 12 | Hurr -20M | 58 | 1 | PT:P2 | 65 | -830 | 5 | 36 | -386 | 2047 | 29 | -444 | -2042
| 79 | 12 | Hurr -20M | 59 | 1 | PT:P3 | 65 | -829 | 5 | 36 | -385 | 2044 | 29 | -443 | -2039
| 79 | 12 | Hurr -20M | 60 | 1 | PT:P4 | 65 | -828 | 5 | 36 | -385 | 2042 | 29 | -443 | -2037
| 80 | 12 | Hurr -15M | 1 | 1 | TL-S1 | 295 | -1242 | 2 | 162 | -607 | 4370 | 134 | -636 | -4369
| 80 | 12 | Hurr -15M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 80 | 12 | Hurr -15M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 80 | 12 | Hurr -15M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 80 | 12 | Hurr -15M | 10 | 1 | ST1 | 799 | -3721 | 10 | 419 | -1801 | 13955 | 380 | -1920 | -13945
| 80 | 12 | Hurr -15M | 10 | 2 | ST2 | 799 | -3698 | 10 | 419 | -1790 | 13956 | 380 | -1908 | -13946
| 80 | 12 | Hurr -15M | 10 | 3 | ST3 | 799 | -3673 | 10 | 419 | -1779 | 13957 | 380 | -1895 | -13948
| 80 | 12 | Hurr -15M | 46 | 1 | F2 | 64 | -497 | 3 | 34 | -233 | 1160 | 30 | -265 | -1157
| 80 | 12 | Hurr -15M | 49 | 1 | S1 | 164 | -1232 | 4 | 89 | -594 | 4507 | 75 | -638 | -4503
| 80 | 12 | Hurr -15M | 49 | 2 | S2 | 164 | -1229 | 4 | 89 | -593 | 4507 | 75 | -636 | -4503
| 80 | 12 | Hurr -15M | 49 | 3 | S3 | 164 | -1226 | 4 | 89 | -592 | 4507 | 75 | -634 | -4504
| 80 | 12 | Hurr -15M | 50 | 1 | S4 | 164 | -1190 | 4 | 89 | -572 | 4510 | 75 | -617 | -4506
| 80 | 12 | Hurr -15M | 50 | 2 | S5 | 164 | -1186 | 4 | 89 | -571 | 4510 | 75 | -615 | -4506
| 80 | 12 | Hurr -15M | 50 | 3 | S6 | 164 | -1182 | 4 | 89 | -569 | 4510 | 75 | -613 | -4506
| 80 | 12 | Hurr -15M | 53 | 1 | S7 | 79 | -531 | 2 | 42 | -252 | 1544 | 37 | -279 | -1542
| 80 | 12 | Hurr -15M | 54 | 1 | S8 | 79 | -516 | 2 | 42 | -244 | 1546 | 37 | -271 | -1544
| 80 | 12 | Hurr -15M | 57 | 1 | PT:P1 | 65 | -872 | 5 | 37 | -410 | 2138 | 29 | -463 | -2133
| 80 | 12 | Hurr -15M | 58 | 1 | PT:P2 | 65 | -871 | 5 | 36 | -409 | 2135 | 29 | -462 | -2131
| 80 | 12 | Hurr -15M | 59 | 1 | PT:P3 | 65 | -870 | 5 | 36 | -409 | 2133 | 29 | -462 | -2128
| 80 | 12 | Hurr -15M | 60 | 1 | PT:P4 | 65 | -869 | 5 | 36 | -408 | 2130 | 29 | -461 | -2126
| 81 | 12 | Hurr -10M | 1 | 1 | TL-S1 | 297 | -1265 | 1 | 163 | -620 | 4417 | 135 | -644 | -4416
| 81 | 12 | Hurr -10M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 81 | 12 | Hurr -10M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 81 | 12 | Hurr -10M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 81 | 12 | Hurr -10M | 10 | 1 | ST1 | 801 | -3798 | 9 | 420 | -1846 | 14135 | 381 | -1952 | -14126
| 81 | 12 | Hurr -10M | 10 | 2 | ST2 | 801 | -3775 | 9 | 420 | -1835 | 14136 | 381 | -1940 | -14127
| 81 | 12 | Hurr -10M | 10 | 3 | ST3 | 801 | -3749 | 9 | 420 | -1823 | 14137 | 381 | -1926 | -14128
| 81 | 12 | Hurr -10M | 46 | 1 | F2 | 64 | -515 | 2 | 34 | -243 | 1195 | 30 | -272 | -1192
| 81 | 12 | Hurr -10M | 49 | 1 | S1 | 165 | -1259 | 3 | 90 | -610 | 4570 | 75 | -649 | -4566
| 81 | 12 | Hurr -10M | 49 | 2 | S2 | 165 | -1256 | 3 | 90 | -609 | 4570 | 75 | -647 | -4567
| 81 | 12 | Hurr -10M | 49 | 3 | S3 | 165 | -1253 | 3 | 90 | -608 | 4570 | 75 | -645 | -4567
| 81 | 12 | Hurr -10M | 50 | 1 | S4 | 164 | -1216 | 3 | 89 | -588 | 4573 | 75 | -628 | -4569
| 81 | 12 | Hurr -10M | 50 | 2 | S5 | 164 | -1212 | 3 | 89 | -586 | 4573 | 75 | -626 | -4569
| 81 | 12 | Hurr -10M | 50 | 3 | S6 | 164 | -1208 | 3 | 89 | -584 | 4573 | 75 | -624 | -4570
| 81 | 12 | Hurr -10M | 53 | 1 | S7 | 79 | -549 | 2 | 42 | -263 | 1588 | 37 | -286 | -1586
| 81 | 12 | Hurr -10M | 54 | 1 | S8 | 79 | -533 | 2 | 42 | -254 | 1589 | 37 | -278 | -1587
| 81 | 12 | Hurr -10M | 57 | 1 | PT:P1 | 66 | -903 | 4 | 37 | -428 | 2202 | 29 | -475 | -2198
| 81 | 12 | Hurr -10M | 58 | 1 | PT:P2 | 66 | -902 | 4 | 37 | -427 | 2200 | 29 | -474 | -2195
| 81 | 12 | Hurr -10M | 59 | 1 | PT:P3 | 66 | -901 | 4 | 37 | -427 | 2197 | 29 | -474 | -2193
| 81 | 12 | Hurr -10M | 60 | 1 | PT:P4 | 65 | -899 | 4 | 37 | -426 | 2194 | 29 | -473 | -2190
| 82 | 12 | Hurr -5M | 1 | 1 | TL-S1 | 299 | -1277 | 1 | 164 | -629 | 4442 | 135 | -648 | -4441
| 82 | 12 | Hurr -5M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 82 | 12 | Hurr -5M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 82 | 12 | Hurr -5M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 82 | 12 | Hurr -5M | 10 | 1 | ST1 | 802 | -3844 | 8 | 421 | -1877 | 14238 | 381 | -1967 | -14230
| 82 | 12 | Hurr -5M | 10 | 2 | ST2 | 802 | -3820 | 7 | 421 | -1865 | 14239 | 381 | -1955 | -14231
| 82 | 12 | Hurr -5M | 10 | 3 | ST3 | 802 | -3794 | 7 | 421 | -1853 | 14240 | 381 | -1941 | -14233
| 82 | 12 | Hurr -5M | 46 | 1 | F2 | 64 | -525 | 2 | 34 | -251 | 1216 | 30 | -275 | -1214
| 82 | 12 | Hurr -5M | 49 | 1 | S1 | 165 | -1275 | 3 | 90 | -622 | 4608 | 75 | -654 | -4605
| 82 | 12 | Hurr -5M | 49 | 2 | S2 | 165 | -1272 | 3 | 90 | -620 | 4608 | 75 | -652 | -4605
| 82 | 12 | Hurr -5M | 49 | 3 | S3 | 165 | -1269 | 3 | 90 | -619 | 4608 | 75 | -650 | -4606
| 82 | 12 | Hurr -5M | 50 | 1 | S4 | 164 | -1233 | 3 | 90 | -599 | 4611 | 75 | -633 | -4608
| 82 | 12 | Hurr -5M | 50 | 2 | S5 | 164 | -1228 | 3 | 90 | -597 | 4611 | 75 | -631 | -4608
| 82 | 12 | Hurr -5M | 50 | 3 | S6 | 164 | -1224 | 3 | 90 | -595 | 4611 | 75 | -629 | -4608
| 82 | 12 | Hurr -5M | 53 | 1 | S7 | 79 | -559 | 2 | 42 | -270 | 1613 | 37 | -290 | -1611
| 82 | 12 | Hurr -5M | 54 | 1 | S8 | 79 | -543 | 2 | 42 | -261 | 1615 | 37 | -282 | -1613
| 82 | 12 | Hurr -5M | 57 | 1 | PT:P1 | 66 | -921 | 3 | 37 | -441 | 2240 | 29 | -480 | -2237
| 82 | 12 | Hurr -5M | 58 | 1 | PT:P2 | 66 | -920 | 3 | 37 | -440 | 2238 | 29 | -480 | -2234
| 82 | 12 | Hurr -5M | 59 | 1 | PT:P3 | 66 | -919 | 3 | 37 | -440 | 2235 | 29 | -479 | -2232
| 82 | 12 | Hurr -5M | 60 | 1 | PT:P4 | 66 | -918 | 3 | 37 | -439 | 2233 | 29 | -479 | -2230
| 83 | 12 | Hurr 0M | 1 | 1 | TL-S1 | 299 | -1280 | 0 | 164 | -634 | 4442 | 135 | -646 | -4441
| 83 | 12 | Hurr 0M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 83 | 12 | Hurr 0M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 83 | 12 | Hurr 0M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 83 | 12 | Hurr 0M | 10 | 1 | ST1 | 802 | -3852 | 6 | 421 | -1890 | 14236 | 381 | -1963 | -14230
| 83 | 12 | Hurr 0M | 10 | 2 | ST2 | 802 | -3828 | 6 | 421 | -1878 | 14238 | 381 | -1950 | -14232
| 83 | 12 | Hurr 0M | 10 | 3 | ST3 | 802 | -3802 | 6 | 421 | -1865 | 14239 | 381 | -1937 | -14233
| 83 | 12 | Hurr 0M | 46 | 1 | F2 | 64 | -527 | 2 | 34 | -254 | 1216 | 30 | -273 | -1214
| 83 | 12 | Hurr 0M | 49 | 1 | S1 | 165 | -1278 | 2 | 90 | -626 | 4608 | 75 | -652 | -4605
| 83 | 12 | Hurr 0M | 49 | 2 | S2 | 165 | -1275 | 2 | 90 | -625 | 4608 | 75 | -650 | -4606
| 83 | 12 | Hurr 0M | 49 | 3 | S3 | 165 | -1272 | 2 | 90 | -624 | 4608 | 75 | -648 | -4606
| 83 | 12 | Hurr 0M | 50 | 1 | S4 | 164 | -1235 | 2 | 90 | -604 | 4611 | 75 | -632 | -4608
| 83 | 12 | Hurr 0M | 50 | 2 | S5 | 164 | -1231 | 2 | 90 | -602 | 4611 | 75 | -629 | -4608
| 83 | 12 | Hurr 0M | 50 | 3 | S6 | 164 | -1227 | 2 | 90 | -600 | 4611 | 75 | -627 | -4609
| 83 | 12 | Hurr 0M | 53 | 1 | S7 | 79 | -561 | 1 | 42 | -273 | 1613 | 37 | -288 | -1611
| 83 | 12 | Hurr 0M | 54 | 1 | S8 | 79 | -545 | 1 | 42 | -264 | 1615 | 37 | -281 | -1613
| 83 | 12 | Hurr 0M | 57 | 1 | PT:P1 | 66 | -924 | 3 | 37 | -446 | 2240 | 29 | -478 | -2237
| 83 | 12 | Hurr 0M | 58 | 1 | PT:P2 | 66 | -923 | 3 | 37 | -446 | 2237 | 29 | -478 | -2235
| 83 | 12 | Hurr 0M | 59 | 1 | PT:P3 | 66 | -922 | 3 | 37 | -445 | 2235 | 29 | -477 | -2232
| 83 | 12 | Hurr 0M | 60 | 1 | PT:P4 | 66 | -921 | 3 | 37 | -445 | 2233 | 29 | -476 | -2230
| 84 | 12 | Hurr 5M | 1 | 1 | TL-S1 | 299 | -1277 | -1 | 164 | -635 | 4441 | 135 | -641 | -4442
| 84 | 12 | Hurr 5M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 84 | 12 | Hurr 5M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 84 | 12 | Hurr 5M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 84 | 12 | Hurr 5M | 10 | 1 | ST1 | 802 | -3842 | 4 | 421 | -1893 | 14236 | 381 | -1948 | -14232
| 84 | 12 | Hurr 5M | 10 | 2 | ST2 | 802 | -3818 | 4 | 421 | -1882 | 14237 | 381 | -1936 | -14233
| 84 | 12 | Hurr 5M | 10 | 3 | ST3 | 802 | -3792 | 4 | 421 | -1869 | 14238 | 381 | -1923 | -14234
| 84 | 12 | Hurr 5M | 46 | 1 | F2 | 64 | -525 | 1 | 34 | -255 | 1215 | 30 | -270 | -1214
| 84 | 12 | Hurr 5M | 49 | 1 | S1 | 165 | -1275 | 2 | 90 | -628 | 4607 | 75 | -646 | -4606
| 84 | 12 | Hurr 5M | 49 | 2 | S2 | 165 | -1272 | 2 | 90 | -627 | 4608 | 75 | -645 | -4606
| 84 | 12 | Hurr 5M | 49 | 3 | S3 | 165 | -1268 | 2 | 90 | -625 | 4608 | 75 | -643 | -4606
| 84 | 12 | Hurr 5M | 50 | 1 | S4 | 164 | -1232 | 2 | 90 | -605 | 4610 | 75 | -626 | -4609
| 84 | 12 | Hurr 5M | 50 | 2 | S5 | 164 | -1228 | 2 | 90 | -603 | 4611 | 75 | -624 | -4609
| 84 | 12 | Hurr 5M | 50 | 3 | S6 | 164 | -1223 | 2 | 90 | -601 | 4611 | 75 | -622 | -4609
| 84 | 12 | Hurr 5M | 53 | 1 | S7 | 79 | -559 | 1 | 42 | -274 | 1613 | 37 | -285 | -1612
| 84 | 12 | Hurr 5M | 54 | 1 | S8 | 79 | -542 | 1 | 42 | -265 | 1615 | 37 | -278 | -1614
| 84 | 12 | Hurr 5M | 57 | 1 | PT:P1 | 66 | -920 | 2 | 37 | -448 | 2240 | 29 | -472 | -2238
| 84 | 12 | Hurr 5M | 58 | 1 | PT:P2 | 66 | -919 | 2 | 37 | -448 | 2237 | 29 | -471 | -2235
| 84 | 12 | Hurr 5M | 59 | 1 | PT:P3 | 66 | -918 | 2 | 37 | -447 | 2235 | 29 | -471 | -2232
| 84 | 12 | Hurr 5M | 60 | 1 | PT:P4 | 66 | -917 | 2 | 37 | -447 | 2232 | 29 | -470 | -2230
| 85 | 12 | Hurr 10M | 1 | 1 | TL-S1 | 297 | -1263 | -1 | 163 | -632 | 4416 | 135 | -631 | -4417
| 85 | 12 | Hurr 10M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 85 | 12 | Hurr 10M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 85 | 12 | Hurr 10M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 85 | 12 | Hurr 10M | 10 | 1 | ST1 | 801 | -3792 | 3 | 420 | -1878 | 14122 | 381 | -1914 | -14119
| 85 | 12 | Hurr 10M | 10 | 2 | ST2 | 801 | -3769 | 3 | 420 | -1866 | 14123 | 381 | -1902 | -14121
| 85 | 12 | Hurr 10M | 10 | 3 | ST3 | 801 | -3743 | 3 | 420 | -1854 | 14124 | 381 | -1890 | -14122
| 85 | 12 | Hurr 10M | 46 | 1 | F2 | 64 | -514 | 1 | 34 | -252 | 1194 | 30 | -262 | -1193
| 85 | 12 | Hurr 10M | 49 | 1 | S1 | 165 | -1257 | 1 | 90 | -623 | 4569 | 75 | -634 | -4568
| 85 | 12 | Hurr 10M | 49 | 2 | S2 | 165 | -1254 | 1 | 90 | -622 | 4569 | 75 | -633 | -4568
| 85 | 12 | Hurr 10M | 49 | 3 | S3 | 165 | -1251 | 1 | 90 | -620 | 4569 | 75 | -631 | -4568
| 85 | 12 | Hurr 10M | 50 | 1 | S4 | 164 | -1215 | 1 | 89 | -600 | 4572 | 75 | -614 | -4570
| 85 | 12 | Hurr 10M | 50 | 2 | S5 | 164 | -1211 | 1 | 89 | -598 | 4572 | 75 | -612 | -4571
| 85 | 12 | Hurr 10M | 50 | 3 | S6 | 164 | -1207 | 1 | 89 | -596 | 4572 | 75 | -610 | -4571
| 85 | 12 | Hurr 10M | 53 | 1 | S7 | 79 | -548 | 1 | 42 | -271 | 1587 | 37 | -277 | -1586
| 85 | 12 | Hurr 10M | 54 | 1 | S8 | 79 | -532 | 1 | 42 | -262 | 1588 | 37 | -270 | -1588
| 85 | 12 | Hurr 10M | 57 | 1 | PT:P1 | 66 | -901 | 1 | 37 | -443 | 2200 | 29 | -458 | -2199
| 85 | 12 | Hurr 10M | 58 | 1 | PT:P2 | 66 | -900 | 1 | 37 | -442 | 2198 | 29 | -457 | -2197
| 85 | 12 | Hurr 10M | 59 | 1 | PT:P3 | 66 | -899 | 1 | 37 | -442 | 2196 | 29 | -457 | -2194
| 85 | 12 | Hurr 10M | 60 | 1 | PT:P4 | 65 | -897 | 1 | 37 | -441 | 2193 | 29 | -456 | -2192
| 86 | 12 | Hurr 15M | 1 | 1 | TL-S1 | 295 | -1240 | -2 | 162 | -624 | 4369 | 134 | -617 | -4370
| 86 | 12 | Hurr 15M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 86 | 12 | Hurr 15M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 86 | 12 | Hurr 15M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 86 | 12 | Hurr 15M | 10 | 1 | ST1 | 799 | -3715 | 1 | 419 | -1849 | 13951 | 380 | -1866 | -13950
| 86 | 12 | Hurr 15M | 10 | 2 | ST2 | 799 | -3692 | 1 | 419 | -1837 | 13952 | 380 | -1855 | -13951
| 86 | 12 | Hurr 15M | 10 | 3 | ST3 | 799 | -3667 | 1 | 419 | -1825 | 13953 | 380 | -1843 | -13952
| 86 | 12 | Hurr 15M | 46 | 1 | F2 | 64 | -496 | 0 | 34 | -245 | 1159 | 30 | -250 | -1158
| 86 | 12 | Hurr 15M | 49 | 1 | S1 | 164 | -1229 | 0 | 89 | -613 | 4505 | 75 | -617 | -4505
| 86 | 12 | Hurr 15M | 49 | 2 | S2 | 164 | -1227 | 0 | 89 | -611 | 4505 | 75 | -615 | -4505
| 86 | 12 | Hurr 15M | 49 | 3 | S3 | 164 | -1223 | 0 | 89 | -610 | 4506 | 75 | -614 | -4505
| 86 | 12 | Hurr 15M | 50 | 1 | S4 | 164 | -1187 | 1 | 89 | -590 | 4508 | 75 | -597 | -4508
| 86 | 12 | Hurr 15M | 50 | 2 | S5 | 164 | -1184 | 1 | 89 | -588 | 4509 | 75 | -595 | -4508
| 86 | 12 | Hurr 15M | 50 | 3 | S6 | 164 | -1180 | 1 | 89 | -586 | 4509 | 75 | -593 | -4508
| 86 | 12 | Hurr 15M | 53 | 1 | S7 | 79 | -530 | 0 | 42 | -264 | 1544 | 37 | -266 | -1543
| 86 | 12 | Hurr 15M | 54 | 1 | S8 | 79 | -514 | 0 | 42 | -255 | 1544 | 37 | -259 | -1544
| 86 | 12 | Hurr 15M | 57 | 1 | PT:P1 | 65 | -870 | 1 | 37 | -432 | 2136 | 29 | -438 | -2135
| 86 | 12 | Hurr 15M | 58 | 1 | PT:P2 | 65 | -869 | 1 | 37 | -431 | 2133 | 29 | -437 | -2133
| 86 | 12 | Hurr 15M | 59 | 1 | PT:P3 | 65 | -867 | 1 | 36 | -431 | 2131 | 29 | -437 | -2130
| 86 | 12 | Hurr 15M | 60 | 1 | PT:P4 | 65 | -866 | 1 | 36 | -430 | 2129 | 29 | -436 | -2128
| 87 | 12 | Hurr 20M | 1 | 1 | TL-S1 | 293 | -1210 | -2 | 160 | -611 | 4309 | 133 | -599 | -4311
| 87 | 12 | Hurr 20M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 87 | 12 | Hurr 20M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 87 | 12 | Hurr 20M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 87 | 12 | Hurr 20M | 10 | 1 | ST1 | 796 | -3607 | 0 | 417 | -1804 | 13702 | 379 | -1803 | -13703
| 87 | 12 | Hurr 20M | 10 | 2 | ST2 | 796 | -3585 | 0 | 417 | -1793 | 13704 | 379 | -1792 | -13704
| 87 | 12 | Hurr 20M | 10 | 3 | ST3 | 796 | -3562 | 0 | 417 | -1781 | 13705 | 379 | -1781 | -13705
| 87 | 12 | Hurr 20M | 46 | 1 | F2 | 64 | -471 | 0 | 34 | -236 | 1110 | 30 | -235 | -1110
| 87 | 12 | Hurr 20M | 49 | 1 | S1 | 164 | -1191 | 0 | 89 | -597 | 4417 | 75 | -594 | -4418
| 87 | 12 | Hurr 20M | 49 | 2 | S2 | 164 | -1188 | 0 | 89 | -596 | 4417 | 75 | -593 | -4418
| 87 | 12 | Hurr 20M | 49 | 3 | S3 | 164 | -1186 | 0 | 89 | -594 | 4418 | 75 | -591 | -4418
| 87 | 12 | Hurr 20M | 50 | 1 | S4 | 163 | -1150 | 0 | 89 | -575 | 4420 | 75 | -575 | -4420
| 87 | 12 | Hurr 20M | 50 | 2 | S5 | 163 | -1146 | 0 | 89 | -573 | 4420 | 75 | -573 | -4420
| 87 | 12 | Hurr 20M | 50 | 3 | S6 | 163 | -1143 | 0 | 89 | -571 | 4421 | 75 | -572 | -4421
| 87 | 12 | Hurr 20M | 53 | 1 | S7 | 78 | -506 | 0 | 41 | -254 | 1484 | 37 | -252 | -1484
| 87 | 12 | Hurr 20M | 54 | 1 | S8 | 78 | -491 | 0 | 41 | -245 | 1485 | 37 | -245 | -1485
| 87 | 12 | Hurr 20M | 57 | 1 | PT:P1 | 65 | -827 | 0 | 36 | -415 | 2047 | 29 | -413 | -2047
| 87 | 12 | Hurr 20M | 58 | 1 | PT:P2 | 65 | -826 | 0 | 36 | -414 | 2044 | 29 | -412 | -2045
| 87 | 12 | Hurr 20M | 59 | 1 | PT:P3 | 65 | -825 | 0 | 36 | -414 | 2042 | 29 | -412 | -2042
| 87 | 12 | Hurr 20M | 60 | 1 | PT:P4 | 65 | -824 | 0 | 36 | -413 | 2040 | 29 | -411 | -2040
| 88 | 12 | Hurr 25M | 1 | 1 | TL-S1 | 289 | -1172 | -3 | 158 | -595 | 4232 | 131 | -577 | -4235
| 88 | 12 | Hurr 25M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 88 | 12 | Hurr 25M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 88 | 12 | Hurr 25M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 88 | 12 | Hurr 25M | 10 | 1 | ST1 | 792 | -3476 | -2 | 414 | -1747 | 13404 | 378 | -1729 | -13406
| 88 | 12 | Hurr 25M | 10 | 2 | ST2 | 792 | -3455 | -2 | 414 | -1736 | 13405 | 378 | -1719 | -13407
| 88 | 12 | Hurr 25M | 10 | 3 | ST3 | 792 | -3433 | -2 | 414 | -1725 | 13406 | 378 | -1708 | -13408
| 88 | 12 | Hurr 25M | 46 | 1 | F2 | 63 | -441 | 0 | 33 | -223 | 1049 | 30 | -218 | -1050
| 88 | 12 | Hurr 25M | 49 | 1 | S1 | 163 | -1144 | -1 | 88 | -577 | 4309 | 75 | -567 | -4310
| 88 | 12 | Hurr 25M | 49 | 2 | S2 | 163 | -1142 | -1 | 88 | -576 | 4309 | 75 | -566 | -4310
| 88 | 12 | Hurr 25M | 49 | 3 | S3 | 163 | -1139 | -1 | 88 | -574 | 4309 | 75 | -565 | -4310
| 88 | 12 | Hurr 25M | 50 | 1 | S4 | 163 | -1104 | -1 | 88 | -555 | 4309 | 75 | -549 | -4310
| 88 | 12 | Hurr 25M | 50 | 2 | S5 | 163 | -1100 | 0 | 88 | -553 | 4309 | 75 | -547 | -4310
| 88 | 12 | Hurr 25M | 50 | 3 | S6 | 163 | -1097 | 0 | 88 | -551 | 4310 | 75 | -546 | -4310
| 88 | 12 | Hurr 25M | 53 | 1 | S7 | 78 | -476 | -1 | 41 | -241 | 1410 | 37 | -235 | -1410
| 88 | 12 | Hurr 25M | 54 | 1 | S8 | 78 | -461 | 0 | 41 | -233 | 1411 | 37 | -229 | -1411
| 88 | 12 | Hurr 25M | 57 | 1 | PT:P1 | 64 | -775 | -1 | 35 | -392 | 1935 | 29 | -383 | -1936
| 88 | 12 | Hurr 25M | 58 | 1 | PT:P2 | 64 | -774 | -1 | 35 | -392 | 1933 | 29 | -382 | -1934
| 88 | 12 | Hurr 25M | 59 | 1 | PT:P3 | 64 | -773 | -1 | 35 | -391 | 1930 | 29 | -382 | -1931
| 88 | 12 | Hurr 25M | 60 | 1 | PT:P4 | 64 | -772 | -1 | 35 | -391 | 1928 | 29 | -381 | -1929
| 89 | 12 | Hurr 30M | 1 | 1 | TL-S1 | 285 | -1128 | -3 | 156 | -576 | 4143 | 130 | -553 | -4146
| 89 | 12 | Hurr 30M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 89 | 12 | Hurr 30M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 89 | 12 | Hurr 30M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 89 | 12 | Hurr 30M | 10 | 1 | ST1 | 788 | -3324 | -3 | 411 | -1679 | 13063 | 377 | -1646 | -13066
| 89 | 12 | Hurr 30M | 10 | 2 | ST2 | 788 | -3305 | -3 | 411 | -1669 | 13064 | 377 | -1637 | -13067
| 89 | 12 | Hurr 30M | 10 | 3 | ST3 | 788 | -3285 | -3 | 411 | -1658 | 13065 | 377 | -1627 | -13068
| 89 | 12 | Hurr 30M | 46 | 1 | F2 | 63 | -406 | -1 | 33 | -208 | 978 | 30 | -199 | -978
| 89 | 12 | Hurr 30M | 49 | 1 | S1 | 163 | -1089 | -2 | 88 | -552 | 4180 | 75 | -537 | -4181
| 89 | 12 | Hurr 30M | 49 | 2 | S2 | 163 | -1087 | -2 | 88 | -551 | 4180 | 75 | -536 | -4181
| 89 | 12 | Hurr 30M | 49 | 3 | S3 | 163 | -1085 | -1 | 88 | -550 | 4180 | 75 | -535 | -4181
| 89 | 12 | Hurr 30M | 50 | 1 | S4 | 163 | -1050 | -1 | 88 | -531 | 4182 | 75 | -519 | -4183
| 89 | 12 | Hurr 30M | 50 | 2 | S5 | 163 | -1047 | -1 | 88 | -529 | 4182 | 75 | -518 | -4183
| 89 | 12 | Hurr 30M | 50 | 3 | S6 | 163 | -1044 | -1 | 88 | -528 | 4183 | 75 | -516 | -4184
| 89 | 12 | Hurr 30M | 53 | 1 | S7 | 77 | -441 | -1 | 40 | -225 | 1322 | 37 | -216 | -1323
| 89 | 12 | Hurr 30M | 54 | 1 | S8 | 77 | -427 | -1 | 40 | -217 | 1323 | 37 | -210 | -1324
| 89 | 12 | Hurr 30M | 57 | 1 | PT:P1 | 63 | -714 | -1 | 35 | -365 | 1803 | 29 | -349 | -1804
| 89 | 12 | Hurr 30M | 58 | 1 | PT:P2 | 63 | -713 | -1 | 35 | -365 | 1801 | 29 | -348 | -1803
| 89 | 12 | Hurr 30M | 59 | 1 | PT:P3 | 63 | -712 | -1 | 35 | -364 | 1799 | 29 | -348 | -1801
| 89 | 12 | Hurr 30M | 60 | 1 | PT:P4 | 63 | -711 | -1 | 35 | -364 | 1797 | 28 | -347 | -1798
| 90 | 12 | Hurr 35M | 1 | 1 | TL-S1 | 281 | -1082 | -4 | 153 | -555 | 4053 | 128 | -527 | -4057
| 90 | 12 | Hurr 35M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 90 | 12 | Hurr 35M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 90 | 12 | Hurr 35M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 90 | 12 | Hurr 35M | 10 | 1 | ST1 | 784 | -3157 | -4 | 408 | -1602 | 12690 | 376 | -1555 | -12694
| 90 | 12 | Hurr 35M | 10 | 2 | ST2 | 784 | -3140 | -4 | 408 | -1592 | 12690 | 376 | -1547 | -12695
| 90 | 12 | Hurr 35M | 10 | 3 | ST3 | 784 | -3121 | -4 | 408 | -1582 | 12691 | 376 | -1539 | -12695
| 90 | 12 | Hurr 35M | 46 | 1 | F2 | 62 | -367 | -1 | 32 | -190 | 896 | 30 | -177 | -897
| 90 | 12 | Hurr 35M | 49 | 1 | S1 | 162 | -1029 | -2 | 87 | -525 | 4039 | 75 | -504 | -4041
| 90 | 12 | Hurr 35M | 49 | 2 | S2 | 162 | -1027 | -2 | 87 | -524 | 4039 | 75 | -503 | -4041
| 90 | 12 | Hurr 35M | 49 | 3 | S3 | 162 | -1025 | -2 | 87 | -523 | 4039 | 75 | -502 | -4041
| 90 | 12 | Hurr 35M | 50 | 1 | S4 | 162 | -991 | -1 | 87 | -504 | 4041 | 75 | -487 | -4043
| 90 | 12 | Hurr 35M | 50 | 2 | S5 | 162 | -989 | -1 | 87 | -502 | 4041 | 75 | -486 | -4043
| 90 | 12 | Hurr 35M | 50 | 3 | S6 | 162 | -986 | -1 | 87 | -501 | 4042 | 75 | -485 | -4043
| 90 | 12 | Hurr 35M | 53 | 1 | S7 | 77 | -402 | -1 | 40 | -207 | 1224 | 37 | -195 | -1225
| 90 | 12 | Hurr 35M | 54 | 1 | S8 | 77 | -389 | -1 | 40 | -200 | 1225 | 37 | -189 | -1226
| 90 | 12 | Hurr 35M | 57 | 1 | PT:P1 | 62 | -646 | -2 | 34 | -334 | 1653 | 28 | -312 | -1655
| 90 | 12 | Hurr 35M | 58 | 1 | PT:P2 | 62 | -645 | -2 | 34 | -334 | 1651 | 28 | -311 | -1653
| 90 | 12 | Hurr 35M | 59 | 1 | PT:P3 | 62 | -644 | -2 | 34 | -333 | 1649 | 28 | -311 | -1651
| 90 | 12 | Hurr 35M | 60 | 1 | PT:P4 | 62 | -643 | -2 | 34 | -333 | 1648 | 28 | -311 | -1650
| 91 | 12 | Hurr 40M | 1 | 1 | TL-S1 | 277 | -1032 | -4 | 151 | -531 | 3955 | 126 | -501 | -3959
| 91 | 12 | Hurr 40M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 91 | 12 | Hurr 40M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 91 | 12 | Hurr 40M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 91 | 12 | Hurr 40M | 10 | 1 | ST1 | 779 | -2980 | -5 | 404 | -1519 | 12302 | 375 | -1462 | -12307
| 91 | 12 | Hurr 40M | 10 | 2 | ST2 | 779 | -2965 | -5 | 404 | -1510 | 12302 | 375 | -1455 | -12308
| 91 | 12 | Hurr 40M | 10 | 3 | ST3 | 779 | -2948 | -5 | 404 | -1501 | 12303 | 375 | -1447 | -12308
| 91 | 12 | Hurr 40M | 46 | 1 | F2 | 62 | -325 | -1 | 32 | -170 | 807 | 30 | -155 | -808
| 91 | 12 | Hurr 40M | 49 | 1 | S1 | 162 | -965 | -2 | 86 | -495 | 3891 | 75 | -470 | -3893
| 91 | 12 | Hurr 40M | 49 | 2 | S2 | 162 | -963 | -2 | 86 | -494 | 3891 | 75 | -470 | -3894
| 91 | 12 | Hurr 40M | 49 | 3 | S3 | 162 | -962 | -2 | 86 | -493 | 3891 | 75 | -469 | -3894
| 91 | 12 | Hurr 40M | 50 | 1 | S4 | 161 | -929 | -2 | 86 | -475 | 3894 | 75 | -454 | -3895
| 91 | 12 | Hurr 40M | 50 | 2 | S5 | 161 | -927 | -2 | 86 | -473 | 3894 | 75 | -453 | -3896
| 91 | 12 | Hurr 40M | 50 | 3 | S6 | 161 | -924 | -2 | 86 | -472 | 3894 | 75 | -452 | -3896
| 91 | 12 | Hurr 40M | 53 | 1 | S7 | 76 | -360 | -1 | 39 | -187 | 1116 | 37 | -173 | -1118
| 91 | 12 | Hurr 40M | 54 | 1 | S8 | 76 | -348 | -1 | 39 | -180 | 1117 | 37 | -168 | -1118
| 91 | 12 | Hurr 40M | 57 | 1 | PT:P1 | 61 | -572 | -2 | 33 | -300 | 1489 | 28 | -273 | -1491
| 91 | 12 | Hurr 40M | 58 | 1 | PT:P2 | 61 | -572 | -2 | 33 | -299 | 1487 | 28 | -272 | -1489
| 91 | 12 | Hurr 40M | 59 | 1 | PT:P3 | 61 | -571 | -2 | 33 | -299 | 1485 | 28 | -272 | -1488
| 91 | 12 | Hurr 40M | 60 | 1 | PT:P4 | 61 | -570 | -2 | 33 | -299 | 1484 | 28 | -272 | -1486
| 92 | 12 | Hurr 45M | 1 | 1 | TL-S1 | 272 | -983 | -4 | 148 | -508 | 3866 | 124 | -475 | -3870
| 92 | 12 | Hurr 45M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 92 | 12 | Hurr 45M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 92 | 12 | Hurr 45M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 92 | 12 | Hurr 45M | 10 | 1 | ST1 | 774 | -2802 | -6 | 401 | -1433 | 11930 | 374 | -1369 | -11936
| 92 | 12 | Hurr 45M | 10 | 2 | ST2 | 774 | -2788 | -6 | 401 | -1426 | 11930 | 374 | -1363 | -11936
| 92 | 12 | Hurr 45M | 10 | 3 | ST3 | 774 | -2774 | -6 | 401 | -1417 | 11931 | 374 | -1356 | -11937
| 92 | 12 | Hurr 45M | 46 | 1 | F2 | 61 | -281 | -2 | 31 | -149 | 712 | 30 | -132 | -713
| 92 | 12 | Hurr 45M | 49 | 1 | S1 | 161 | -900 | -3 | 86 | -464 | 3742 | 75 | -436 | -3744
| 92 | 12 | Hurr 45M | 49 | 2 | S2 | 161 | -899 | -3 | 86 | -463 | 3742 | 75 | -436 | -3744
| 92 | 12 | Hurr 45M | 49 | 3 | S3 | 161 | -897 | -3 | 86 | -462 | 3742 | 75 | -435 | -3745
| 92 | 12 | Hurr 45M | 50 | 1 | S4 | 161 | -865 | -2 | 86 | -444 | 3744 | 75 | -421 | -3746
| 92 | 12 | Hurr 45M | 50 | 2 | S5 | 161 | -863 | -2 | 86 | -443 | 3744 | 75 | -420 | -3746
| 92 | 12 | Hurr 45M | 50 | 3 | S6 | 161 | -861 | -2 | 86 | -442 | 3744 | 75 | -419 | -3746
| 92 | 12 | Hurr 45M | 53 | 1 | S7 | 75 | -316 | -2 | 38 | -166 | 1003 | 37 | -150 | -1005
| 92 | 12 | Hurr 45M | 54 | 1 | S8 | 75 | -306 | -1 | 38 | -160 | 1004 | 37 | -146 | -1005
| 92 | 12 | Hurr 45M | 57 | 1 | PT:P1 | 60 | -496 | -3 | 32 | -263 | 1313 | 28 | -233 | -1316
| 92 | 12 | Hurr 45M | 58 | 1 | PT:P2 | 60 | -495 | -3 | 32 | -263 | 1312 | 28 | -232 | -1315
| 92 | 12 | Hurr 45M | 59 | 1 | PT:P3 | 60 | -495 | -3 | 32 | -263 | 1310 | 28 | -232 | -1313
| 92 | 12 | Hurr 45M | 60 | 1 | PT:P4 | 60 | -494 | -3 | 32 | -262 | 1309 | 28 | -232 | -1312
| 93 | 12 | Hurr 50M | 1 | 1 | TL-S1 | 269 | -934 | -4 | 146 | -484 | 3781 | 123 | -450 | -3786
| 93 | 12 | Hurr 50M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 93 | 12 | Hurr 50M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 93 | 12 | Hurr 50M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 93 | 12 | Hurr 50M | 10 | 1 | ST1 | 770 | -2626 | -6 | 398 | -1348 | 11574 | 373 | -1278 | -11580
| 93 | 12 | Hurr 50M | 10 | 2 | ST2 | 770 | -2614 | -6 | 398 | -1341 | 11575 | 373 | -1273 | -11581
| 93 | 12 | Hurr 50M | 10 | 3 | ST3 | 770 | -2601 | -6 | 398 | -1334 | 11575 | 373 | -1268 | -11581
| 93 | 12 | Hurr 50M | 46 | 1 | F2 | 61 | -237 | -2 | 31 | -128 | 613 | 30 | -109 | -615
| 93 | 12 | Hurr 50M | 49 | 1 | S1 | 161 | -836 | -3 | 85 | -433 | 3601 | 76 | -404 | -3604
| 93 | 12 | Hurr 50M | 49 | 2 | S2 | 161 | -835 | -3 | 85 | -432 | 3601 | 76 | -403 | -3604
| 93 | 12 | Hurr 50M | 49 | 3 | S3 | 161 | -834 | -3 | 85 | -431 | 3601 | 76 | -403 | -3604
| 93 | 12 | Hurr 50M | 50 | 1 | S4 | 160 | -803 | -2 | 85 | -414 | 3604 | 75 | -389 | -3606
| 93 | 12 | Hurr 50M | 50 | 2 | S5 | 160 | -801 | -2 | 85 | -413 | 3604 | 75 | -388 | -3606
| 93 | 12 | Hurr 50M | 50 | 3 | S6 | 160 | -799 | -2 | 85 | -412 | 3604 | 75 | -387 | -3606
| 93 | 12 | Hurr 50M | 53 | 1 | S7 | 75 | -272 | -2 | 38 | -145 | 889 | 37 | -127 | -890
| 93 | 12 | Hurr 50M | 54 | 1 | S8 | 74 | -263 | -1 | 38 | -139 | 889 | 37 | -124 | -890
| 93 | 12 | Hurr 50M | 57 | 1 | PT:P1 | 59 | -418 | -3 | 31 | -225 | 1132 | 28 | -193 | -1135
| 93 | 12 | Hurr 50M | 58 | 1 | PT:P2 | 59 | -418 | -3 | 31 | -225 | 1131 | 28 | -193 | -1134
| 93 | 12 | Hurr 50M | 59 | 1 | PT:P3 | 59 | -417 | -3 | 31 | -225 | 1129 | 28 | -192 | -1132
| 93 | 12 | Hurr 50M | 60 | 1 | PT:P4 | 59 | -417 | -3 | 31 | -225 | 1128 | 28 | -192 | -1131
| 94 | 12 | Hurr 55M | 1 | 1 | TL-S1 | 265 | -890 | -4 | 144 | -462 | 3714 | 121 | -428 | -3718
| 94 | 12 | Hurr 55M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 94 | 12 | Hurr 55M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 94 | 12 | Hurr 55M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 94 | 12 | Hurr 55M | 10 | 1 | ST1 | 767 | -2463 | -6 | 395 | -1267 | 11277 | 372 | -1196 | -11283
| 94 | 12 | Hurr 55M | 10 | 2 | ST2 | 767 | -2452 | -6 | 395 | -1261 | 11278 | 372 | -1192 | -11284
| 94 | 12 | Hurr 55M | 10 | 3 | ST3 | 767 | -2441 | -6 | 395 | -1254 | 11278 | 372 | -1187 | -11284
| 94 | 12 | Hurr 55M | 46 | 1 | F2 | 60 | -193 | -2 | 30 | -106 | 515 | 30 | -87 | -517
| 94 | 12 | Hurr 55M | 49 | 1 | S1 | 160 | -777 | -3 | 85 | -403 | 3475 | 76 | -374 | -3478
| 94 | 12 | Hurr 55M | 49 | 2 | S2 | 160 | -776 | -3 | 85 | -403 | 3475 | 76 | -373 | -3478
| 94 | 12 | Hurr 55M | 49 | 3 | S3 | 160 | -775 | -3 | 85 | -402 | 3475 | 76 | -373 | -3478
| 94 | 12 | Hurr 55M | 50 | 1 | S4 | 160 | -745 | -2 | 84 | -385 | 3477 | 75 | -360 | -3479
| 94 | 12 | Hurr 55M | 50 | 2 | S5 | 160 | -743 | -2 | 84 | -384 | 3477 | 75 | -359 | -3480
| 94 | 12 | Hurr 55M | 50 | 3 | S6 | 160 | -741 | -2 | 84 | -383 | 3477 | 75 | -358 | -3480
| 94 | 12 | Hurr 55M | 53 | 1 | S7 | 74 | -230 | -2 | 37 | -124 | 777 | 37 | -106 | -779
| 94 | 12 | Hurr 55M | 54 | 1 | S8 | 74 | -222 | -1 | 37 | -119 | 777 | 37 | -103 | -779
| 94 | 12 | Hurr 55M | 57 | 1 | PT:P1 | 58 | -342 | -3 | 30 | -188 | 950 | 28 | -155 | -953
| 94 | 12 | Hurr 55M | 58 | 1 | PT:P2 | 58 | -342 | -3 | 30 | -187 | 949 | 28 | -154 | -952
| 94 | 12 | Hurr 55M | 59 | 1 | PT:P3 | 58 | -341 | -3 | 30 | -187 | 947 | 28 | -154 | -950
| 94 | 12 | Hurr 55M | 60 | 1 | PT:P4 | 58 | -341 | -3 | 30 | -187 | 946 | 28 | -154 | -949
| 95 | 12 | Hurr 60M | 1 | 1 | TL-S1 | 263 | -851 | -4 | 143 | -442 | 3659 | 120 | -409 | -3663
| 95 | 12 | Hurr 60M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 95 | 12 | Hurr 60M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 95 | 12 | Hurr 60M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 95 | 12 | Hurr 60M | 10 | 1 | ST1 | 764 | -2315 | -6 | 393 | -1192 | 11040 | 371 | -1123 | -11047
| 95 | 12 | Hurr 60M | 10 | 2 | ST2 | 764 | -2306 | -6 | 393 | -1187 | 11041 | 371 | -1120 | -11047
| 95 | 12 | Hurr 60M | 10 | 3 | ST3 | 764 | -2297 | -6 | 393 | -1181 | 11041 | 371 | -1116 | -11047
| 95 | 12 | Hurr 60M | 46 | 1 | F2 | 59 | -152 | -2 | 30 | -86 | 421 | 30 | -67 | -422
| 95 | 12 | Hurr 60M | 49 | 1 | S1 | 160 | -723 | -3 | 84 | -376 | 3369 | 76 | -347 | -3372
| 95 | 12 | Hurr 60M | 49 | 2 | S2 | 160 | -723 | -3 | 84 | -375 | 3369 | 76 | -347 | -3372
| 95 | 12 | Hurr 60M | 49 | 3 | S3 | 160 | -722 | -3 | 84 | -375 | 3369 | 76 | -347 | -3372
| 95 | 12 | Hurr 60M | 50 | 1 | S4 | 159 | -692 | -2 | 84 | -358 | 3371 | 75 | -334 | -3373
| 95 | 12 | Hurr 60M | 50 | 2 | S5 | 159 | -691 | -2 | 84 | -358 | 3371 | 75 | -333 | -3373
| 95 | 12 | Hurr 60M | 50 | 3 | S6 | 159 | -689 | -2 | 84 | -357 | 3371 | 75 | -333 | -3374
| 95 | 12 | Hurr 60M | 53 | 1 | S7 | 73 | -190 | -2 | 37 | -104 | 675 | 37 | -87 | -677
| 95 | 12 | Hurr 60M | 54 | 1 | S8 | 73 | -183 | -1 | 37 | -99 | 676 | 37 | -84 | -677
| 95 | 12 | Hurr 60M | 57 | 1 | PT:P1 | 57 | -270 | -3 | 29 | -151 | 773 | 28 | -119 | -776
| 95 | 12 | Hurr 60M | 58 | 1 | PT:P2 | 57 | -269 | -3 | 29 | -151 | 772 | 28 | -119 | -775
| 95 | 12 | Hurr 60M | 59 | 1 | PT:P3 | 57 | -269 | -3 | 29 | -151 | 771 | 28 | -118 | -774
| 95 | 12 | Hurr 60M | 60 | 1 | PT:P4 | 57 | -269 | -3 | 29 | -150 | 770 | 28 | -118 | -773
| 96 | 12 | Hurr 65M | 1 | 1 | TL-S1 | 261 | -817 | -4 | 141 | -424 | 3617 | 120 | -393 | -3621
| 96 | 12 | Hurr 65M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 96 | 12 | Hurr 65M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 96 | 12 | Hurr 65M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 96 | 12 | Hurr 65M | 10 | 1 | ST1 | 762 | -2186 | -6 | 391 | -1125 | 10865 | 370 | -1062 | -10871
| 96 | 12 | Hurr 65M | 10 | 2 | ST2 | 761 | -2179 | -5 | 391 | -1121 | 10866 | 370 | -1059 | -10871
| 96 | 12 | Hurr 65M | 10 | 3 | ST3 | 761 | -2171 | -5 | 391 | -1116 | 10866 | 370 | -1055 | -10871
| 96 | 12 | Hurr 65M | 46 | 1 | F2 | 59 | -115 | -1 | 29 | -66 | 336 | 30 | -49 | -338
| 96 | 12 | Hurr 65M | 49 | 1 | S1 | 159 | -679 | -2 | 84 | -353 | 3295 | 76 | -326 | -3298
| 96 | 12 | Hurr 65M | 49 | 2 | S2 | 159 | -678 | -2 | 84 | -352 | 3295 | 76 | -326 | -3298
| 96 | 12 | Hurr 65M | 49 | 3 | S3 | 159 | -678 | -2 | 84 | -352 | 3295 | 76 | -326 | -3298
| 96 | 12 | Hurr 65M | 50 | 1 | S4 | 159 | -648 | -2 | 84 | -336 | 3297 | 75 | -313 | -3299
| 96 | 12 | Hurr 65M | 50 | 2 | S5 | 159 | -647 | -2 | 84 | -335 | 3297 | 75 | -312 | -3299
| 96 | 12 | Hurr 65M | 50 | 3 | S6 | 159 | -646 | -2 | 84 | -334 | 3297 | 75 | -312 | -3299
| 96 | 12 | Hurr 65M | 53 | 1 | S7 | 73 | -156 | -1 | 36 | -86 | 590 | 37 | -70 | -591
| 96 | 12 | Hurr 65M | 54 | 1 | S8 | 73 | -150 | -1 | 36 | -82 | 590 | 37 | -68 | -591
| 96 | 12 | Hurr 65M | 57 | 1 | PT:P1 | 56 | -204 | -3 | 28 | -117 | 611 | 28 | -87 | -614
| 96 | 12 | Hurr 65M | 58 | 1 | PT:P2 | 56 | -204 | -3 | 28 | -117 | 611 | 28 | -87 | -614
| 96 | 12 | Hurr 65M | 59 | 1 | PT:P3 | 56 | -203 | -3 | 28 | -117 | 610 | 28 | -87 | -613
| 96 | 12 | Hurr 65M | 60 | 1 | PT:P4 | 56 | -203 | -3 | 28 | -116 | 610 | 28 | -87 | -612
| 97 | 12 | Hurr 70M | 1 | 1 | TL-S1 | 260 | -791 | -3 | 141 | -409 | 3597 | 119 | -382 | -3600
| 97 | 12 | Hurr 70M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 97 | 12 | Hurr 70M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 97 | 12 | Hurr 70M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 97 | 12 | Hurr 70M | 10 | 1 | ST1 | 760 | -2082 | -5 | 390 | -1068 | 10763 | 370 | -1013 | -10768
| 97 | 12 | Hurr 70M | 10 | 2 | ST2 | 760 | -2075 | -5 | 390 | -1065 | 10763 | 370 | -1011 | -10768
| 97 | 12 | Hurr 70M | 10 | 3 | ST3 | 760 | -2069 | -5 | 390 | -1061 | 10763 | 370 | -1008 | -10768
| 97 | 12 | Hurr 70M | 46 | 1 | F2 | 59 | -84 | -1 | 29 | -50 | 268 | 30 | -35 | -269
| 97 | 12 | Hurr 70M | 49 | 1 | S1 | 159 | -643 | -2 | 83 | -333 | 3248 | 76 | -310 | -3250
| 97 | 12 | Hurr 70M | 49 | 2 | S2 | 159 | -643 | -2 | 83 | -333 | 3248 | 76 | -310 | -3250
| 97 | 12 | Hurr 70M | 49 | 3 | S3 | 159 | -643 | -2 | 83 | -333 | 3248 | 76 | -310 | -3250
| 97 | 12 | Hurr 70M | 50 | 1 | S4 | 159 | -613 | -2 | 83 | -317 | 3249 | 75 | -297 | -3251
| 97 | 12 | Hurr 70M | 50 | 2 | S5 | 159 | -613 | -2 | 83 | -316 | 3249 | 75 | -296 | -3251
| 97 | 12 | Hurr 70M | 50 | 3 | S6 | 159 | -612 | -2 | 83 | -316 | 3249 | 75 | -296 | -3251
| 97 | 12 | Hurr 70M | 53 | 1 | S7 | 72 | -129 | -1 | 36 | -71 | 528 | 37 | -57 | -529
| 97 | 12 | Hurr 70M | 54 | 1 | S8 | 72 | -123 | -1 | 36 | -68 | 528 | 37 | -55 | -529
| 97 | 12 | Hurr 70M | 57 | 1 | PT:P1 | 55 | -148 | -2 | 27 | -87 | 477 | 28 | -61 | -479
| 97 | 12 | Hurr 70M | 58 | 1 | PT:P2 | 55 | -148 | -2 | 27 | -87 | 477 | 28 | -61 | -479
| 97 | 12 | Hurr 70M | 59 | 1 | PT:P3 | 55 | -148 | -2 | 27 | -87 | 476 | 28 | -61 | -479
| 97 | 12 | Hurr 70M | 60 | 1 | PT:P4 | 55 | -148 | -2 | 27 | -87 | 476 | 28 | -61 | -478
| 98 | 12 | Hurr 75M | 1 | 1 | TL-S1 | 259 | -770 | -3 | 141 | -397 | 3585 | 119 | -373 | -3588
| 98 | 12 | Hurr 75M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 98 | 12 | Hurr 75M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 98 | 12 | Hurr 75M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 98 | 12 | Hurr 75M | 10 | 1 | ST1 | 760 | -2001 | -4 | 390 | -1023 | 10723 | 370 | -978 | -10727
| 98 | 12 | Hurr 75M | 10 | 2 | ST2 | 760 | -1996 | -4 | 390 | -1019 | 10724 | 370 | -976 | -10727
| 98 | 12 | Hurr 75M | 10 | 3 | ST3 | 760 | -1990 | -4 | 390 | -1016 | 10724 | 370 | -974 | -10728
| 98 | 12 | Hurr 75M | 46 | 1 | F2 | 58 | -61 | -1 | 28 | -37 | 223 | 30 | -25 | -224
| 98 | 12 | Hurr 75M | 49 | 1 | S1 | 159 | -617 | -2 | 83 | -318 | 3221 | 76 | -299 | -3223
| 98 | 12 | Hurr 75M | 49 | 2 | S2 | 159 | -617 | -2 | 83 | -318 | 3221 | 76 | -299 | -3223
| 98 | 12 | Hurr 75M | 49 | 3 | S3 | 159 | -617 | -2 | 83 | -318 | 3221 | 76 | -299 | -3223
| 98 | 12 | Hurr 75M | 50 | 1 | S4 | 159 | -587 | -1 | 83 | -302 | 3223 | 75 | -286 | -3224
| 98 | 12 | Hurr 75M | 50 | 2 | S5 | 159 | -587 | -1 | 83 | -301 | 3223 | 75 | -285 | -3224
| 98 | 12 | Hurr 75M | 50 | 3 | S6 | 159 | -586 | -1 | 83 | -301 | 3223 | 75 | -285 | -3224
| 98 | 12 | Hurr 75M | 53 | 1 | S7 | 72 | -109 | -1 | 36 | -60 | 492 | 37 | -49 | -493
| 98 | 12 | Hurr 75M | 54 | 1 | S8 | 72 | -104 | -1 | 36 | -57 | 492 | 36 | -47 | -493
| 98 | 12 | Hurr 75M | 57 | 1 | PT:P1 | 54 | -106 | -2 | 26 | -63 | 384 | 28 | -43 | -386
| 98 | 12 | Hurr 75M | 58 | 1 | PT:P2 | 54 | -106 | -2 | 26 | -63 | 384 | 28 | -43 | -386
| 98 | 12 | Hurr 75M | 59 | 1 | PT:P3 | 54 | -106 | -2 | 26 | -63 | 384 | 28 | -43 | -386
| 98 | 12 | Hurr 75M | 60 | 1 | PT:P4 | 54 | -106 | -2 | 26 | -63 | 384 | 28 | -43 | -386
| 99 | 12 | Hurr 80M | 1 | 1 | TL-S1 | 259 | -756 | -2 | 140 | -387 | 3582 | 119 | -369 | -3584
| 99 | 12 | Hurr 80M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 99 | 12 | Hurr 80M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 99 | 12 | Hurr 80M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 99 | 12 | Hurr 80M | 10 | 1 | ST1 | 759 | -1939 | -3 | 390 | -985 | 10705 | 370 | -954 | -10707
| 99 | 12 | Hurr 80M | 10 | 2 | ST2 | 759 | -1935 | -3 | 390 | -982 | 10705 | 370 | -952 | -10707
| 99 | 12 | Hurr 80M | 10 | 3 | ST3 | 759 | -1930 | -3 | 390 | -979 | 10705 | 370 | -951 | -10708
| 99 | 12 | Hurr 80M | 46 | 1 | F2 | 58 | -46 | -1 | 28 | -27 | 202 | 30 | -19 | -203
| 99 | 12 | Hurr 80M | 49 | 1 | S1 | 159 | -599 | -1 | 83 | -306 | 3212 | 76 | -293 | -3213
| 99 | 12 | Hurr 80M | 49 | 2 | S2 | 159 | -599 | -1 | 83 | -306 | 3212 | 76 | -293 | -3213
| 99 | 12 | Hurr 80M | 49 | 3 | S3 | 159 | -600 | -1 | 83 | -307 | 3212 | 76 | -293 | -3213
| 99 | 12 | Hurr 80M | 50 | 1 | S4 | 159 | -570 | -1 | 83 | -290 | 3213 | 75 | -279 | -3214
| 99 | 12 | Hurr 80M | 50 | 2 | S5 | 159 | -569 | -1 | 83 | -290 | 3213 | 75 | -279 | -3214
| 99 | 12 | Hurr 80M | 50 | 3 | S6 | 159 | -569 | -1 | 83 | -290 | 3213 | 75 | -279 | -3214
| 99 | 12 | Hurr 80M | 53 | 1 | S7 | 72 | -97 | -1 | 35 | -52 | 477 | 37 | -44 | -477
| 99 | 12 | Hurr 80M | 54 | 1 | S8 | 72 | -92 | -1 | 35 | -49 | 477 | 36 | -42 | -478
| 99 | 12 | Hurr 80M | 57 | 1 | PT:P1 | 54 | -79 | -1 | 26 | -47 | 339 | 28 | -32 | -341
| 99 | 12 | Hurr 80M | 58 | 1 | PT:P2 | 54 | -79 | -1 | 26 | -47 | 339 | 28 | -32 | -341
| 99 | 12 | Hurr 80M | 59 | 1 | PT:P3 | 54 | -79 | -1 | 26 | -47 | 339 | 28 | -32 | -341
| 99 | 12 | Hurr 80M | 60 | 1 | PT:P4 | 54 | -79 | -1 | 26 | -47 | 339 | 28 | -32 | -341
| 100 | 12 | Hurr 85M | 1 | 1 | TL-S1 | 259 | -747 | -1 | 140 | -380 | 3583 | 119 | -367 | -3584
| 100 | 12 | Hurr 85M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 100 | 12 | Hurr 85M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 100 | 12 | Hurr 85M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 100 | 12 | Hurr 85M | 10 | 1 | ST1 | 759 | -1897 | -1 | 390 | -956 | 10706 | 370 | -941 | -10708
| 100 | 12 | Hurr 85M | 10 | 2 | ST2 | 759 | -1893 | -1 | 390 | -954 | 10707 | 370 | -939 | -10708
| 100 | 12 | Hurr 85M | 10 | 3 | ST3 | 759 | -1889 | -1 | 390 | -951 | 10707 | 370 | -938 | -10708
| 100 | 12 | Hurr 85M | 46 | 1 | F2 | 58 | -39 | 0 | 28 | -21 | 197 | 30 | -17 | -198
| 100 | 12 | Hurr 85M | 49 | 1 | S1 | 159 | -590 | -1 | 83 | -299 | 3212 | 76 | -291 | -3213
| 100 | 12 | Hurr 85M | 49 | 2 | S2 | 159 | -590 | -1 | 83 | -299 | 3212 | 76 | -291 | -3213
| 100 | 12 | Hurr 85M | 49 | 3 | S3 | 159 | -590 | -1 | 83 | -299 | 3212 | 76 | -292 | -3213
| 100 | 12 | Hurr 85M | 50 | 1 | S4 | 159 | -560 | 0 | 83 | -283 | 3214 | 75 | -278 | -3214
| 100 | 12 | Hurr 85M | 50 | 2 | S5 | 159 | -560 | 0 | 83 | -283 | 3214 | 75 | -277 | -3214
| 100 | 12 | Hurr 85M | 50 | 3 | S6 | 159 | -560 | 0 | 83 | -282 | 3214 | 75 | -277 | -3214
| 100 | 12 | Hurr 85M | 53 | 1 | S7 | 72 | -90 | 0 | 35 | -47 | 473 | 37 | -43 | -474
| 100 | 12 | Hurr 85M | 54 | 1 | S8 | 72 | -85 | 0 | 35 | -44 | 474 | 36 | -41 | -474
| 100 | 12 | Hurr 85M | 57 | 1 | PT:P1 | 54 | -66 | -1 | 26 | -37 | 328 | 28 | -29 | -329
| 100 | 12 | Hurr 85M | 58 | 1 | PT:P2 | 54 | -66 | -1 | 26 | -37 | 328 | 28 | -29 | -329
| 100 | 12 | Hurr 85M | 59 | 1 | PT:P3 | 54 | -66 | -1 | 26 | -37 | 328 | 28 | -29 | -329
| 100 | 12 | Hurr 85M | 60 | 1 | PT:P4 | 54 | -66 | -1 | 26 | -37 | 328 | 28 | -29 | -329
| 101 | 12 | Hurr 90M | 1 | 1 | TL-S1 | 259 | -740 | -1 | 140 | -375 | 3583 | 119 | -365 | -3585
| 101 | 12 | Hurr 90M | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 101 | 12 | Hurr 90M | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 101 | 12 | Hurr 90M | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0
| 101 | 12 | Hurr 90M | 10 | 1 | ST1 | 759 | -1864 | -1 | 390 | -935 | 10707 | 370 | -928 | -10708
| 101 | 12 | Hurr 90M | 10 | 2 | ST2 | 759 | -1860 | -1 | 390 | -933 | 10708 | 370 | -927 | -10708
| 101 | 12 | Hurr 90M | 10 | 3 | ST3 | 759 | -1856 | -1 | 390 | -931 | 10708 | 370 | -925 | -10708
| 101 | 12 | Hurr 90M | 46 | 1 | F2 | 58 | -34 | 0 | 28 | -18 | 198 | 30 | -16 | -198
| 101 | 12 | Hurr 90M | 49 | 1 | S1 | 159 | -583 | 0 | 83 | -294 | 3213 | 76 | -289 | -3213
| 101 | 12 | Hurr 90M | 49 | 2 | S2 | 159 | -583 | 0 | 83 | -294 | 3213 | 76 | -289 | -3213
| 101 | 12 | Hurr 90M | 49 | 3 | S3 | 159 | -584 | 0 | 83 | -294 | 3213 | 76 | -290 | -3213
| 101 | 12 | Hurr 90M | 50 | 1 | S4 | 159 | -554 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 101 | 12 | Hurr 90M | 50 | 2 | S5 | 159 | -554 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 101 | 12 | Hurr 90M | 50 | 3 | S6 | 159 | -553 | 0 | 83 | -278 | 3214 | 75 | -276 | -3214
| 101 | 12 | Hurr 90M | 53 | 1 | S7 | 72 | -86 | 0 | 35 | -44 | 474 | 37 | -42 | -474
| 101 | 12 | Hurr 90M | 54 | 1 | S8 | 72 | -81 | 0 | 35 | -42 | 474 | 36 | -40 | -474
| 101 | 12 | Hurr 90M | 57 | 1 | PT:P1 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 101 | 12 | Hurr 90M | 58 | 1 | PT:P2 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 101 | 12 | Hurr 90M | 59 | 1 | PT:P3 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 101 | 12 | Hurr 90M | 60 | 1 | PT:P4 | 54 | -58 | 0 | 26 | -31 | 328 | 28 | -27 | -329
| 114 | 6 | Broken Wire, 9:1 | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 114 | 6 | Broken Wire, 9:1 | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 114 | 6 | Broken Wire, 9:1 | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 114 | 6 | Broken Wire, 9:1 | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 114 | 6 | Broken Wire, 9:1 | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 114 | 6 | Broken Wire, 9:1 | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 114 | 6 | Broken Wire, 9:1 | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 114 | 6 | Broken Wire, 9:1 | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 114 | 6 | Broken Wire, 9:1 | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 114 | 6 | Broken Wire, 9:1 | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 114 | 6 | Broken Wire, 9:1 | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 114 | 6 | Broken Wire, 9:1 | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 114 | 6 | Broken Wire, 9:1 | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 114 | 6 | Broken Wire, 9:1 | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 114 | 6 | Broken Wire, 9:1 | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 114 | 6 | Broken Wire, 9:1 | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 114 | 6 | Broken Wire, 9:1 | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 114 | 6 | Broken Wire, 9:1 | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 114 | 6 | Broken Wire, 9:1 | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 114 | 6 | Broken Wire, 9:1 | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 115 | 6 | Broken Wire, 9:2 | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 115 | 6 | Broken Wire, 9:2 | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 115 | 6 | Broken Wire, 9:2 | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 115 | 6 | Broken Wire, 9:2 | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 115 | 6 | Broken Wire, 9:2 | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 115 | 6 | Broken Wire, 9:2 | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 115 | 6 | Broken Wire, 9:2 | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 115 | 6 | Broken Wire, 9:2 | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 115 | 6 | Broken Wire, 9:2 | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 115 | 6 | Broken Wire, 9:2 | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 115 | 6 | Broken Wire, 9:2 | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 115 | 6 | Broken Wire, 9:2 | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 115 | 6 | Broken Wire, 9:2 | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 115 | 6 | Broken Wire, 9:2 | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 115 | 6 | Broken Wire, 9:2 | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 115 | 6 | Broken Wire, 9:2 | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 115 | 6 | Broken Wire, 9:2 | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 115 | 6 | Broken Wire, 9:2 | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 115 | 6 | Broken Wire, 9:2 | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 115 | 6 | Broken Wire, 9:2 | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 116 | 6 | Broken Wire, 9:3 | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 116 | 6 | Broken Wire, 9:3 | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 116 | 6 | Broken Wire, 9:3 | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 116 | 6 | Broken Wire, 9:3 | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 116 | 6 | Broken Wire, 9:3 | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 116 | 6 | Broken Wire, 9:3 | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 116 | 6 | Broken Wire, 9:3 | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 116 | 6 | Broken Wire, 9:3 | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 116 | 6 | Broken Wire, 9:3 | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 116 | 6 | Broken Wire, 9:3 | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 116 | 6 | Broken Wire, 9:3 | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 116 | 6 | Broken Wire, 9:3 | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 116 | 6 | Broken Wire, 9:3 | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 116 | 6 | Broken Wire, 9:3 | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 116 | 6 | Broken Wire, 9:3 | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 116 | 6 | Broken Wire, 9:3 | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 116 | 6 | Broken Wire, 9:3 | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 116 | 6 | Broken Wire, 9:3 | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 116 | 6 | Broken Wire, 9:3 | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 116 | 6 | Broken Wire, 9:3 | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 117 | 6 | Broken Wire, 9:1 AHD | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 117 | 6 | Broken Wire, 9:1 AHD | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 117 | 6 | Broken Wire, 9:1 AHD | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 117 | 6 | Broken Wire, 9:1 AHD | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 117 | 6 | Broken Wire, 9:1 AHD | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 117 | 6 | Broken Wire, 9:1 AHD | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 117 | 6 | Broken Wire, 9:1 AHD | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 117 | 6 | Broken Wire, 9:1 AHD | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 117 | 6 | Broken Wire, 9:1 AHD | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 117 | 6 | Broken Wire, 9:1 AHD | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 117 | 6 | Broken Wire, 9:1 AHD | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 117 | 6 | Broken Wire, 9:1 AHD | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 117 | 6 | Broken Wire, 9:1 AHD | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 117 | 6 | Broken Wire, 9:1 AHD | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 117 | 6 | Broken Wire, 9:1 AHD | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 117 | 6 | Broken Wire, 9:1 AHD | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 117 | 6 | Broken Wire, 9:1 AHD | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 117 | 6 | Broken Wire, 9:1 AHD | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 117 | 6 | Broken Wire, 9:1 AHD | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 117 | 6 | Broken Wire, 9:1 AHD | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 118 | 6 | Broken Wire, 9:2 AHD | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 118 | 6 | Broken Wire, 9:2 AHD | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 118 | 6 | Broken Wire, 9:2 AHD | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 118 | 6 | Broken Wire, 9:2 AHD | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 118 | 6 | Broken Wire, 9:2 AHD | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 118 | 6 | Broken Wire, 9:2 AHD | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 118 | 6 | Broken Wire, 9:2 AHD | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 118 | 6 | Broken Wire, 9:2 AHD | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 118 | 6 | Broken Wire, 9:2 AHD | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 118 | 6 | Broken Wire, 9:2 AHD | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 118 | 6 | Broken Wire, 9:2 AHD | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 118 | 6 | Broken Wire, 9:2 AHD | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 118 | 6 | Broken Wire, 9:2 AHD | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 118 | 6 | Broken Wire, 9:2 AHD | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 118 | 6 | Broken Wire, 9:2 AHD | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 118 | 6 | Broken Wire, 9:2 AHD | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 118 | 6 | Broken Wire, 9:2 AHD | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 118 | 6 | Broken Wire, 9:2 AHD | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 118 | 6 | Broken Wire, 9:2 AHD | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 118 | 6 | Broken Wire, 9:2 AHD | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 119 | 6 | Broken Wire, 9:3 AHD | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 119 | 6 | Broken Wire, 9:3 AHD | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 119 | 6 | Broken Wire, 9:3 AHD | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 119 | 6 | Broken Wire, 9:3 AHD | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 119 | 6 | Broken Wire, 9:3 AHD | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 119 | 6 | Broken Wire, 9:3 AHD | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 119 | 6 | Broken Wire, 9:3 AHD | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 119 | 6 | Broken Wire, 9:3 AHD | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 119 | 6 | Broken Wire, 9:3 AHD | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 119 | 6 | Broken Wire, 9:3 AHD | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 119 | 6 | Broken Wire, 9:3 AHD | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 119 | 6 | Broken Wire, 9:3 AHD | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 119 | 6 | Broken Wire, 9:3 AHD | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 119 | 6 | Broken Wire, 9:3 AHD | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 119 | 6 | Broken Wire, 9:3 AHD | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 119 | 6 | Broken Wire, 9:3 AHD | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 119 | 6 | Broken Wire, 9:3 AHD | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 119 | 6 | Broken Wire, 9:3 AHD | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 119 | 6 | Broken Wire, 9:3 AHD | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 119 | 6 | Broken Wire, 9:3 AHD | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 120 | 6 | Broken Wire, 9:1 BCK | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 120 | 6 | Broken Wire, 9:1 BCK | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 120 | 6 | Broken Wire, 9:1 BCK | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 120 | 6 | Broken Wire, 9:1 BCK | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 120 | 6 | Broken Wire, 9:1 BCK | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 120 | 6 | Broken Wire, 9:1 BCK | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 120 | 6 | Broken Wire, 9:1 BCK | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 120 | 6 | Broken Wire, 9:1 BCK | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 120 | 6 | Broken Wire, 9:1 BCK | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 120 | 6 | Broken Wire, 9:1 BCK | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 120 | 6 | Broken Wire, 9:1 BCK | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 120 | 6 | Broken Wire, 9:1 BCK | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 120 | 6 | Broken Wire, 9:1 BCK | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 120 | 6 | Broken Wire, 9:1 BCK | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 120 | 6 | Broken Wire, 9:1 BCK | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 120 | 6 | Broken Wire, 9:1 BCK | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 120 | 6 | Broken Wire, 9:1 BCK | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 120 | 6 | Broken Wire, 9:1 BCK | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 120 | 6 | Broken Wire, 9:1 BCK | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 120 | 6 | Broken Wire, 9:1 BCK | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 121 | 6 | Broken Wire, 9:2 BCK | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 121 | 6 | Broken Wire, 9:2 BCK | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 121 | 6 | Broken Wire, 9:2 BCK | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 121 | 6 | Broken Wire, 9:2 BCK | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 121 | 6 | Broken Wire, 9:2 BCK | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 121 | 6 | Broken Wire, 9:2 BCK | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 121 | 6 | Broken Wire, 9:2 BCK | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 121 | 6 | Broken Wire, 9:2 BCK | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 121 | 6 | Broken Wire, 9:2 BCK | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 121 | 6 | Broken Wire, 9:2 BCK | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 121 | 6 | Broken Wire, 9:2 BCK | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 121 | 6 | Broken Wire, 9:2 BCK | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 121 | 6 | Broken Wire, 9:2 BCK | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 121 | 6 | Broken Wire, 9:2 BCK | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 121 | 6 | Broken Wire, 9:2 BCK | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 121 | 6 | Broken Wire, 9:2 BCK | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 121 | 6 | Broken Wire, 9:2 BCK | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 121 | 6 | Broken Wire, 9:2 BCK | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 121 | 6 | Broken Wire, 9:2 BCK | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 121 | 6 | Broken Wire, 9:2 BCK | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 122 | 6 | Broken Wire, 9:3 BKC | 1 | 1 | TL-S1 | 259 | -678 | -1 | 140 | -342 | 3281 | 119 | -336 | -3282 | Global wind towards 0 (deg) for max usage (into bisector). | 692.3041
| 122 | 6 | Broken Wire, 9:3 BKC | 9 | 1 | T1 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 122 | 6 | Broken Wire, 9:3 BKC | 9 | 2 | T2 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 122 | 6 | Broken Wire, 9:3 BKC | 9 | 3 | T3 | 96 | 0 | 0 | 0 | 0 | 0 | 96 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 122 | 6 | Broken Wire, 9:3 BKC | 10 | 1 | ST1 | 761 | -1709 | 0 | 391 | -854 | 9815 | 371 | -855 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1753.1577
| 122 | 6 | Broken Wire, 9:3 BKC | 10 | 2 | ST2 | 761 | -1705 | 0 | 391 | -852 | 9816 | 371 | -854 | -9815 | Global wind towards 0 (deg) for max usage (into bisector). | 1749.2587
| 122 | 6 | Broken Wire, 9:3 BKC | 10 | 3 | ST3 | 761 | -1702 | 0 | 391 | -850 | 9816 | 371 | -852 | -9816 | Global wind towards 0 (deg) for max usage (into bisector). | 1746.3347
| 122 | 6 | Broken Wire, 9:3 BKC | 46 | 1 | F2 | 60 | -31 | 0 | 29 | -16 | 181 | 31 | -16 | -181 | Global wind towards 0 (deg) for max usage (into bisector). | 42.45
| 122 | 6 | Broken Wire, 9:3 BKC | 49 | 1 | S1 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 122 | 6 | Broken Wire, 9:3 BKC | 49 | 2 | S2 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 122 | 6 | Broken Wire, 9:3 BKC | 49 | 3 | S3 | 161 | -535 | 0 | 84 | -268 | 2945 | 76 | -267 | -2945 | Global wind towards 0 (deg) for max usage (into bisector). | 541.5542
| 122 | 6 | Broken Wire, 9:3 BKC | 50 | 1 | S4 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 122 | 6 | Broken Wire, 9:3 BKC | 50 | 2 | S5 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 122 | 6 | Broken Wire, 9:3 BKC | 50 | 3 | S6 | 160 | -507 | 0 | 84 | -253 | 2941 | 76 | -254 | -2941 | Global wind towards 0 (deg) for max usage (into bisector). | 513.9115
| 122 | 6 | Broken Wire, 9:3 BKC | 53 | 1 | S7 | 73 | -79 | 0 | 36 | -40 | 434 | 37 | -39 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 86.8159
| 122 | 6 | Broken Wire, 9:3 BKC | 54 | 1 | S8 | 73 | -75 | 0 | 36 | -37 | 434 | 37 | -37 | -434 | Global wind towards 0 (deg) for max usage (into bisector). | 83.1925
| 122 | 6 | Broken Wire, 9:3 BKC | 57 | 1 | PT:P1 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 122 | 6 | Broken Wire, 9:3 BKC | 58 | 1 | PT:P2 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 122 | 6 | Broken Wire, 9:3 BKC | 59 | 1 | PT:P3 | 54 | -53 | 0 | 26 | -27 | 300 | 28 | -27 | -300 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 122 | 6 | Broken Wire, 9:3 BKC | 60 | 1 | PT:P4 | 54 | -53 | 0 | 26 | -27 | 301 | 28 | -27 | -301 | Global wind towards 0 (deg) for max usage (into bisector). | 59.0339
| 125 | 6 | 2% Deflection | 1 | 1 | TL-S1 | 219 | -545 | -1 | 118 | -275 | 2636 | 101 | -270 | -2637 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 10 | 1 | ST1 | 692 | -1553 | 0 | 355 | -776 | 8923 | 337 | -777 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1593.0581
| 125 | 6 | 2% Deflection | 10 | 2 | ST2 | 692 | -1550 | 0 | 355 | -774 | 8923 | 337 | -776 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1590.1336
| 125 | 6 | 2% Deflection | 10 | 3 | ST3 | 692 | -1547 | 0 | 355 | -773 | 8923 | 337 | -774 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1587.2095
| 125 | 6 | 2% Deflection | 46 | 1 | F2 | 55 | -28 | 0 | 27 | -14 | 162 | 28 | -14 | -162 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 49 | 1 | S1 | 141 | -297 | 0 | 71 | -149 | 1637 | 70 | -148 | -1637 | Global wind towards 0 (deg) for max usage (into bisector). | 305.3686
| 125 | 6 | 2% Deflection | 49 | 2 | S2 | 141 | -297 | 0 | 71 | -149 | 1637 | 70 | -148 | -1637 | Global wind towards 0 (deg) for max usage (into bisector). | 305.3686
| 125 | 6 | 2% Deflection | 49 | 3 | S3 | 141 | -298 | 0 | 71 | -149 | 1637 | 70 | -149 | -1637 | Global wind towards 0 (deg) for max usage (into bisector). | 306.3413
| 125 | 6 | 2% Deflection | 50 | 1 | S4 | 141 | -282 | 0 | 71 | -141 | 1638 | 70 | -141 | -1638 | Global wind towards 0 (deg) for max usage (into bisector). | 290.8006
| 125 | 6 | 2% Deflection | 50 | 2 | S5 | 141 | -282 | 0 | 71 | -141 | 1638 | 70 | -141 | -1638 | Global wind towards 0 (deg) for max usage (into bisector). | 290.8006
| 125 | 6 | 2% Deflection | 50 | 3 | S6 | 141 | -282 | 0 | 71 | -141 | 1638 | 70 | -141 | -1638 | Global wind towards 0 (deg) for max usage (into bisector). | 290.8006
| 125 | 6 | 2% Deflection | 53 | 1 | S7 | 67 | -66 | 0 | 33 | -33 | 361 | 34 | -33 | -361 | Global wind towards 0 (deg) for max usage (into bisector). | 73.7902
| 125 | 6 | 2% Deflection | 54 | 1 | S8 | 66 | -62 | 0 | 33 | -31 | 361 | 34 | -31 | -361 | Global wind towards 0 (deg) for max usage (into bisector). | 70.2353
| 125 | 6 | 2% Deflection | 57 | 1 | PT:P1 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 58 | 1 | PT:P2 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 59 | 1 | PT:P3 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 125 | 6 | 2% Deflection | 60 | 1 | PT:P4 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 1 | 1 | TL-S1 | 236 | -616 | -1 | 128 | -311 | 2983 | 108 | -305 | -2983 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 9 | 1 | T1 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 9 | 2 | T2 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 9 | 3 | T3 | 87 | 0 | 0 | 0 | 0 | 0 | 87 | 0 | 0 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 10 | 1 | ST1 | 692 | -1553 | 0 | 355 | -776 | 8923 | 337 | -777 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1593.0581
| 126 | 6 | Normal Everyday | 10 | 2 | ST2 | 692 | -1550 | 0 | 355 | -774 | 8923 | 337 | -776 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1590.1336
| 126 | 6 | Normal Everyday | 10 | 3 | ST3 | 692 | -1547 | 0 | 355 | -773 | 8923 | 337 | -774 | -8923 | Global wind towards 0 (deg) for max usage (into bisector). | 1587.2095
| 126 | 6 | Normal Everyday | 46 | 1 | F2 | 55 | -28 | 0 | 27 | -14 | 164 | 28 | -14 | -164 | Global wind towards 0 (deg) for max usage (into bisector). | Global wind towards 0 (deg) for max usage (into bisector).
| 126 | 6 | Normal Everyday | 49 | 1 | S1 | 146 | -486 | 0 | 76 | -243 | 2677 | 70 | -243 | -2677 | Global wind towards 0 (deg) for max usage (into bisector). | 491.9065
| 126 | 6 | Normal Everyday | 49 | 2 | S2 | 146 | -486 | 0 | 76 | -244 | 2677 | 70 | -243 | -2677 | Global wind towards 0 (deg) for max usage (into bisector). | 491.9065
| 126 | 6 | Normal Everyday | 49 | 3 | S3 | 146 | -487 | 0 | 76 | -244 | 2677 | 70 | -243 | -2677 | Global wind towards 0 (deg) for max usage (into bisector). | 492.8945
| 126 | 6 | Normal Everyday | 50 | 1 | S4 | 145 | -461 | 0 | 76 | -230 | 2674 | 69 | -231 | -2674 | Global wind towards 0 (deg) for max usage (into bisector). | 467.2226
| 126 | 6 | Normal Everyday | 50 | 2 | S5 | 145 | -461 | 0 | 76 | -230 | 2674 | 69 | -231 | -2674 | Global wind towards 0 (deg) for max usage (into bisector). | 467.2226
| 126 | 6 | Normal Everyday | 50 | 3 | S6 | 145 | -460 | 0 | 76 | -230 | 2674 | 69 | -231 | -2674 | Global wind towards 0 (deg) for max usage (into bisector). | 466.236
| 126 | 6 | Normal Everyday | 53 | 1 | S7 | 67 | -72 | 0 | 33 | -36 | 395 | 34 | -36 | -395 | Global wind towards 0 (deg) for max usage (into bisector). | 79.2023
| 126 | 6 | Normal Everyday | 54 | 1 | S8 | 67 | -68 | 0 | 33 | -34 | 395 | 34 | -34 | -395 | Global wind towards 0 (deg) for max usage (into bisector). | 75.5844
| 126 | 6 | Normal Everyday | 57 | 1 | PT:P1 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | 53.6656
| 126 | 6 | Normal Everyday | 58 | 1 | PT:P2 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | 53.6656
| 126 | 6 | Normal Everyday | 59 | 1 | PT:P3 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | 53.6656
| 126 | 6 | Normal Everyday | 60 | 1 | PT:P4 | 49 | -48 | 0 | 24 | -24 | 273 | 25 | -24 | -273 | Global wind towards 0 (deg) for max usage (into bisector). | 53.6656
0

## Spacing
| Dist. From Pole Top | Spacing to Next Point | Feet | Inches | Architectural | Load Tree Spacing
ST | 0.11 |  |  |  |  | 10.9167
|  | 2.765 | 2 | 9.18 | 2' 9 9/50"
PT:TL-BV1 | 2.875
|  | 7.5417 | 7 | 6.5004 | 7' 6 1/2"
PT:TL-TR1 | 10.9167
|  | 0.9583 | 0 | 11.4996 | 0' 11 1/2" | 9.5
PT:TL-BV2 | 12.375
|  | 7.5417 | 7 | 6.5004 | 7' 6 1/2"
PT:TL-TR2 | 20.4167
|  | 0.9583 | 0 | 11.4996 | 0' 11 1/2" | 9.5
PT:TL-BV3 | 21.875
|  | 8.0417 | 8 | 0.5004 | 8' 0 1/2"
PT:TL-TR3 | 29.9167
|  | 11 | 10 | 11.9996 | 10' 12" | 11
PT:TL-F1 | 40.9167
|  | 10.0033 | 10 | 0.03996 | 10' 0 1/25" | 10.0033
PT:UB-D1 | 50.92
|  | 3 | 3 | 0 | 3' 0" | 3
PT:UB-D2 | 53.92
|  | 3 | 3 | 0 | 3' 0" | 3
PT:UB-D3 | 56.92
|  | 6.5 | 6 | 6 | 6' 6" | 6.5
PT:UB-D4 | 63.42
|  | 3.333 | 3 | 3.996 | 3' 4" | 3.333
PT:P1 | 66.753
|  | 0.333 | 0 | 3.996 | 0' 4" | 0.333
PT:P2 | 67.086
|  | 0.333 | 0 | 3.996 | 0' 4" | 0.333
PT:P3 | 67.419
|  | 0.333 | 0 | 3.996 | 0' 4" | 0.333
PT:P4 | 67.752
Note on C5: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Needed to subtract off 6" since brace post dimensions are to the bolts
Note on C7: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Accounting for bolt to vang dimension