## Sheet1
LOAD CONDITION |  | TEMP | ICE | WIND | OVERLOAD FACTORS
Description |  | °F | Radial (in) | Pressure (psf) | ANGLE | TRANSVERSE | VERTICAL | LONGITUINDAL
1 - NESC LIGHT (250B) |  | 30 | 0 | 9 | 1.65 | 2.5 | 1.5 | 1.65
2 - NESC EXTREME WIND (250C) |  | 60 | 0 | 28.22 | 1.1 | 1.1 | 1.1 | 1.2
3 - NESC COMBINED ICE & WIND (250D) |  | 15 | 0.5 | 2.3 | 1 | 1 | 1 | 1
4 - NORMAL EVERYDAY |  | 60 | 0 | 0 | 1 | 1 | 1 | 1
5 - 2% POLE DEFLECTION |  | 60 | 0 | 0 | 1 | 1 | 1 | 1
6 - FULL BREAK (NESC 250B) |  | 30 | 0 | 9 | 1.65 | 2.5 | 1.5 | 1.65
7 - FULL BREAK (NESC 250D |  | 15 | 0.5 | 2.3 | 1 | 1 | 1 | 1
LOAD CASE ID: |  | LC1, NESC LIGHT (250B) | [6 empty] | LOAD CASE ID: |  | LC2, NESC EXTREME WIND (250C) |  | LOAD CASE ID: |  | LC3, NESC COMBINED ICE AND WIND (250D)
WIND ON STRUCTURE: |  | 9 | [6 empty] | WIND ON STRUCTURE: |  | 28.22 |  | WIND ON STRUCTURE: |  | 2.3
ATTACHMENT | V | T | L | [5 empty] | ATTACHMENT | V | T | L | ATTACHMENT | V | T | L
S1 | -100 | -1100 | -2000 | [5 empty] | S1 | -100 | -1100 | -1100 | S1 | 200 | -700 | -1100
P1,A | 200 | -4300 | -1400 | [5 empty] | P1,A | -100 | -4100 | -600 | P1,A | 400 | -2500 | -900
P1,B | 200 | -4300 | -1400 | [5 empty] | P1,B | -100 | -4100 | -600 | P1,B | 400 | -2500 | -900
P1,C | 200 | -4300 | -1400 | [5 empty] | P1,C | -100 | -4100 | -600 | P1,C | 400 | -2500 | -900
F1 | 100 | -500 | -100 | [5 empty] | F1 | -100 | -600 | -100 | F1 | 200 | -200 | -100
D1,A & D2,A | -400 | -1200 | -2300 | [5 empty] | D1,A & D2,A | -400 | -1100 | -1100 | D1,A & D2,A | -200 | -600 | -1200
D1,B & D2,B | -400 | -1200 | -2300 | [5 empty] | D1,B & D2,B | -400 | -1100 | -1100 | D1,B & D2,B | -200 | -600 | -1200
D1,C & D2,C | -400 | -1200 | -2300 | [5 empty] | D1,C & D2,C | -400 | -1100 | -1100 | D1,C & D2,C | -200 | -600 | -1200
N1 & N2 | -100 | -600 | 1400 | [5 empty] | N1 & N2 | -200 | -600 | 800 | N1 & N2 | 100 | -300 | 900
C1 | -100 | -700 | -100 | [5 empty] | C1 | -200 | -900 | -100 | C1 | 200 | -300 | -100
C2 | -100 | -700 | -100 | [5 empty] | C2 | -200 | -900 | -100 | C2 | 200 | -300 | -100
C3 | -100 | -700 | -100 | [5 empty] | C3 | -200 | -900 | -100 | C3 | 200 | -300 | -100
C4 | -100 | -700 | -100 | [5 empty] | C4 | -200 | -900 | -100 | C4 | 200 | -300 | -100
ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S | [6 empty] | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S |  | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S
LOAD CASE ID: |  | LC4, NORMAL EVERYDAY | [6 empty] | LOAD CASE ID: |  | LC 5, 2% POLE DEFLECTION |  | LOAD CASE ID: |  | LC6, FULL BREAK (250B)
WIND ON STRUCTURE: |  | 0 | [6 empty] | WIND ON STRUCTURE: |  | 0 |  | WIND ON STRUCTURE: |  | 9
ATTACHMENT | V | T | L | [5 empty] | ATTACHMENT | V | T | L | ATTACHMENT | V | T | L
S1 | 100 | -400 | -1200 | [5 empty] | S1 | 100 | -400 | -1000 | S1 | -200 | -700 | -6800
P1,A | 300 | -1500 | -900 | [5 empty] | P1,A | 300 | -1500 | -800 | P1,A | -500 | -2200 | -20200
P1,B | 300 | -1500 | -900 | [5 empty] | P1,B | 300 | -1500 | -800 | P1,B | -500 | -2200 | -20200
P1,C | 300 | -1500 | -900 | [5 empty] | P1,C | 300 | -1500 | -800 | P1,C | -500 | -2200 | -20200
F1 | 100 | -100 | -100 | [5 empty] | F1 | 100 | -100 | -100 | F1 | -100 | -200 | -900
D1,A & D2,A | -200 | -300 | -1300 | [5 empty] | D1,A & D2,A | -100 | -200 | -600 | D1,A & D2,A | -400 | -500 | -6900
D1,B & D2,B | -200 | -300 | -1300 | [5 empty] | D1,B & D2,B | -100 | -200 | -600 | D1,B & D2,B | -400 | -500 | -6900
D1,C & D2,C | -200 | -300 | -1300 | [5 empty] | D1,C & D2,C | -100 | -200 | -600 | D1,C & D2,C | -400 | -500 | -6900
N1 & N2 | -100 | -100 | 700 | [5 empty] | N1 & N2 | 100 | -100 | 400 | N1 & N2 | -100 | -100 | 3000
C1 | 100 | -100 | -100 | [5 empty] | C1 | 100 | -100 | -100 | C1 | -100 | -400 | -1800
C2 | 100 | -100 | -100 | [5 empty] | C2 | 100 | -100 | -100 | C2 | -100 | -400 | -1800
C3 | 100 | -100 | -100 | [5 empty] | C3 | 100 | -100 | -100 | C3 | -100 | -400 | -1800
C4 | 100 | -100 | -100 | [5 empty] | C4 | 100 | -100 | -100 | C4 | -100 | -400 | -1800
ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S | [6 empty] | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S |  | ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S
POLE TOP DEFLECTION LIMITED TO 2% OF POLE HEIGHT.
LOAD CASE ID: |  | LC7, Full Break (250D)
WIND ON STRUCTURE: |  | 2.3
ATTACHMENT | V | T | L
S1 | -100 | -400 | -4700
P1,A | -300 | -1300 | -14700
P1,B | -300 | -1300 | -14700
P1,C | -300 | -1300 | -14700
F1 | 100 | -100 | -900
D1,A & D2,A | -300 | -300 | -5000
D1,B & D2,B | -300 | -300 | -5000
D1,C & D2,C | -300 | -300 | -5000
N1 & N2 | 100 | -100 | 2400
C1 | 100 | -200 | -1500
C2 | 100 | -200 | -1500
C3 | 100 | -200 | -1500
C4 | 100 | -200 | -1500
ADDITIONAL NOTES: |  | ALL LOADS INCLUDE APPLICABLE OLF'S
| -4.4 | -1096.7 | -1997.6 | [6 empty] | -13.2 | -1020.8 | -1095.6 |  | 155.1 | -650.1 | -1083.5
| 136.4 | -4252.6 | -1399.2 | [6 empty] | -20.9 | -4040.3 | -580.8 |  | 397.1 | -2444.2 | -811.8
| 136.4 | -4252.6 | -1399.2 | [6 empty] | -20.9 | -4040.3 | -580.8 |  | 397.1 | -2444.2 | -811.8
| 136.4 | -4252.6 | -1399.2 | [6 empty] | -20.9 | -4040.3 | -580.8 |  | 397.1 | -2444.2 | -811.8
| 7.7 | -410.3 | -38.5 | [6 empty] | -63.8 | -533.5 | -51.7 |  | 144.1 | -168.3 | -12.1
| -353.1 | -1102.2 | -2241.8 | [6 empty] | -301.4 | -1057.1 | -1080.2 |  | -138.6 | -576.4 | -1194.6
| -353.1 | -1102.2 | -2241.8 | [6 empty] | -301.4 | -1057.1 | -1080.2 |  | -138.6 | -576.4 | -1194.6
| -353.1 | -1102.2 | -2241.8 | [6 empty] | -301.4 | -1057.1 | -1080.2 |  | -138.6 | -575.3 | -1194.6
| -72.6 | -525.8 | 1378.3 | [6 empty] | -112.2 | -542.3 | 720.5 |  | 50.6 | -297 | 849.2
| -64.9 | -699.6 | -83.6 | [6 empty] | -161.7 | -844.8 | -37.4 |  | 172.7 | -237.6 | -33
| -64.9 | -699.6 | -83.6 | [6 empty] | -161.7 | -844.8 | -37.4 |  | 172.7 | -237.6 | -33
| -64.9 | -699.6 | -83.6 | [6 empty] | -161.7 | -844.8 | -37.4 |  | 172.7 | -237.6 | -33
| -64.9 | -699.6 | -83.6 | [6 empty] | -161.7 | -844.8 | -37.4 |  | 172.7 | -237.6 | -33
| 7.7 | -366.3 | -1193.5 | [6 empty] | 20.9 | -328.9 | -962.5 |  | -137.5 | -602.8 | -6702.3
| 237.6 | -1433.3 | -842.6 | [6 empty] | 246.4 | -1416.8 | -761.2 |  | -429 | -2125.2 | -20114.6
| 237.6 | -1433.3 | -842.6 | [6 empty] | 246.4 | -1416.8 | -761.2 |  | -429 | -2125.2 | -20114.6
| 237.6 | -1433.3 | -842.6 | [6 empty] | 246.4 | -1416.8 | -761.2 |  | -429 | -2125.2 | -20114.6
| 36.3 | -18.7 | -16.5 | [6 empty] | 36.3 | -18.7 | -15.4 |  | -20.9 | -191.4 | -873.4
| -118.8 | -251.9 | -1294.7 | [6 empty] | -5.5 | -166.1 | -532.4 |  | -390.5 | -492.8 | -6850.8
| -118.8 | -251.9 | -1294.7 | [6 empty] | -5.5 | -166.1 | -532.4 |  | -390.5 | -492.8 | -6850.8
| -118.8 | -251.9 | -1294.7 | [6 empty] | -5.5 | -166.1 | -532.4 |  | -390.5 | -492.8 | -6850.8
| -1.1 | -85.8 | 656.7 | [6 empty] | 8.8 | -67.1 | 399.3 |  | -7.7 | -14.3 | 2977.7
| 26.4 | -27.5 | -25.3 | [6 empty] | 26.4 | -27.5 | -24.2 |  | -80.3 | -325.6 | -1719.3
| 26.4 | -27.5 | -25.3 | [6 empty] | 26.4 | -27.5 | -24.2 |  | -80.3 | -325.6 | -1719.3
| 26.4 | -27.5 | -25.3 | [6 empty] | 26.4 | -27.5 | -24.2 |  | -80.3 | -325.6 | -1719.3
| 26.4 | -27.5 | -25.3 | [6 empty] | 26.4 | -27.5 | -24.2 |  | -80.3 | -325.6 | -1719.3
| -45.1 | -358.6 | -4667.3
| -234.3 | -1232 | -14620.1
| -234.3 | -1232 | -14620.1
| -234.3 | -1232 | -14620.1
| 37.4 | -80.3 | -808.5
| -253 | -245.3 | -4950
| -253 | -245.3 | -4950
| -253 | -245.3 | -4950
| 70.4 | -88 | 2373.8
| 29.7 | -114.4 | -1400.3
| 29.7 | -114.4 | -1400.3
| 29.7 | -114.4 | -1400.3
| 29.7 | -114.4 | -1400.3